## Temperature
Input | High SP | Low SP | Output | Action | DEVICE | Mapping
XF:23IDA-OP:0{Msk:1}T:1-I | 75 degC | 40 degC | FE Shutter | Close | PT100 | Slot 10 Ch 0
XF:23IDA-OP:0{Msk:1}T:2-I | 75 degC | 40 degC | FE Shutter | Close | PT100 | Slot 10 Ch 1
XF:23IDA-OP:1{Mir:1-Msk}T:1-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 2 Ch 0
XF:23IDA-OP:1{Mir:1-Msk}T:2-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 2 Ch 1
XF:23IDA-OP:1{Mir:1}T:1-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 1 Ch 0
XF:23IDA-OP:1{Mir:1}T:2-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 1 Ch 1
XF:23IDA-OP:1{Msk:1}T:1-I | 75 degC | 40 degC | FE Shutter | Close | PT100 | Slot 11 Ch 0
XF:23IDA-OP:1{Msk:1}T:2-I | 75 degC | 40 degC | FE Shutter | Close | PT100 | Slot 11 Ch 1
XF:23IDA-OP:1{FS:1}T-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 3 Ch 0
XF:23IDA-OP:2{Mir:1A-Msk}T:1-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 4 Ch 1
XF:23IDA-OP:2{Mir:1B-Msk}T:1-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 6 Ch 1
XF:23IDA-OP:2{Mir:1A}T:1-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 3 Ch 1
XF:23IDA-OP:2{Mir:1B}T:1-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 5 Ch 1
XF:23IDA-OP:2{Mir:1A-Msk}T:2-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 5 Ch 0
XF:23IDA-OP:2{Mir:1B-Msk}T:2-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 7 Ch 0
XF:23IDA-OP:2{Mir:1A}T:2-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 4 Ch 0
XF:23IDA-OP:2{Mir:1B}T:2-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 6 Ch 0
XF:23IDA-OP:2{Msk:1}T:1-I | 75 degC | 40 degC | FE Shutter | Close | PT100 | Slot 12 Ch 0
XF:23IDA-OP:2{Msk:1}T:2-I | 75 degC | 40 degC | FE Shutter | Close | PT100 | Slot 12 Ch 1
XF:23IDA-VA:0{DP:1}T-I | 75 degC | 40 degC | FE Shutter | Close | K-Type | Slot 7 Ch 1
XF:23ID1-OP{Diag:02}T-I | 75 degC | 40 degC | Shutter 1 | Close | K-Type
XF:23ID1-OP{Mon-Mir}T-I | 75 degC | 40 degC | Shutter 1 | Close | K-Type
XF:23ID1-OP{Mon-Mir:Msk}T-I | 75 degC | 40 degC | Shutter 1 | Close | K-Type
XF:23ID1-OP{Mon-Grg:1}T-I | 75 degC | 40 degC | Shutter 1 | Close | K-Type
XF:23ID1-OP{Mon-Grg:2}T-I | 75 degC | 40 degC | Shutter 1 | Close | K-Type
XF:23ID1-OP{Mon-Grg:3}T-I | 75 degC | 40 degC | Shutter 1 | Close | K-Type
XF:23ID1-OP{Mon-Grg:4}T-I | 75 degC | 40 degC | Shutter 1 | Close | K-Type
XF:23ID1-OP(Mir:3-Bdr}T-I | 75 degC | 40 degC | XF:23ID1-CT{MC:04} | Disable 48V | K-Type
XF:23ID2-OP{Diag:01}T-I | 75 degC | 40 degC | Shutter 2 | Close | K-Type
XF:23ID2-OP{Mon-Mir}T-I | 75 degC | 40 degC | Shutter 2 | Close | K-Type
XF:23ID2-OP{Mon-Mir:Msk}T-I | 75 degC | 40 degC | Shutter 2 | Close | K-Type
XF:23ID2-OP{Mon-Grg:1}T-I | 75 degC | 40 degC | Shutter 2 | Close | K-Type
XF:23ID2-OP{Mon-Grg:2}T-I | 75 degC | 40 degC | Shutter 2 | Close | K-Type
XF:23ID2-OP{Mon-Grg:3}T-I | 75 degC | 40 degC | Shutter 2 | Close | K-Type
XF:23ID2-OP{Mon-Grg:4}T-I | 75 degC | 40 degC | Shutter 2 | Close | K-Type
XF:23ID2-OP{Chop}T-I | 75 degC | 40 degC | XF:23ID1-CT{???} | Disable 48V | K-Type

## Vacuum
CSX Vacuum Logic
Definitions
(BEAM ON FE) = (FE SHUTTER OPEN) |  |  |  | (SHUTTER 1) = XF:23IDA-OP:1{SSh:1}
(BEAM ON 1) = (FE SHUTTER OPEN) && (XF:23IDA-OP:1{SSh:1}) |  |  |  | (SHUTTER 2) = XF:23IDA-OP:2{SSh:1}
(BEAM ON 2) = (FE SHUTTER OPEN) && (XF:23IDA-OP:2{SSh:1})
Device | Operation | Device | Operation | Device | Operation | Device | Operation | Device | Operation | Device | Operation | Device | Operation | Device | Operation | Device |  |  | Action | Action | Action | Action | Action | NOTES
23IDA (FOE)
XF:23IDA-VA:0{Diag:1-CCG:1} | AND | XF:23IDA-VA:0{Diag:1-IP:1} | AND | XF:23IDA-VA:0{Msk:1-CCG:1} | AND | XF:23IDA-VA:0{Msk:1-IP:1} | AND | XF:23IDA-VA:0{DP:1-IP:1} | AND | XF:23IDA-VA:1{Mir:1-CCG:1} | AND | XF:23IDA-VA:1{Mir:1-IP:1} | AND | XF:23IDA-VA:0{Diag:1-TCG:1} | AND | XF:23IDA-VA:0{Msk:1-TCG:1} | AND | XF:23IDA-VA:1{Mir:1-TCG:1} | ENABLE(XF:23IDA-VA:0{DP:1-GV:1}) | Vacuum Good Signal to FE
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | [10 empty] | CLOSE(FE SHUTTER)
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) |  |  |  |  | AND | NOT(BEAM ON FE) |  |  |  |  | CLOSE(XF:23IDA-VA:0{DP:1-GV:1})
NOT(BEAM ON FE) | AND | REQUEST CLOSE | [16 empty] | CLOSE(XF:23IDA-VA:0{DP:1-GV:1})
XF:23IDA-VA:1{Mir:1-CCG:1} | AND | XF:23IDA-VA:1{Mir:1-IP:1} | AND | XF:23IDA-VA:1{FS:1-CCG:1} | AND | XF:23IDA-VA:1{FS:1-IP:1} | AND | XF:23IDA-VA:1{Mir:1-TCG:1} | AND | XF:23IDA-VA:1{FS:1-TCG:1} | [8 empty] | ENABLE(XF:23IDA-VA:1{Mir:1-GV:1})
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(FE SHUTTER)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON FE) | [14 empty] | CLOSE(XF:23IDA-VA:1{Mir:1-GV:1}) | CLOSE(XF:23IDA-VA:0{DP:1-GV:1})
NOT(BEAM ON FE) | AND | REQUEST CLOSE | [16 empty] | CLOSE(XF:23IDA-VA:1{Mir:1-GV:1})
XF:23IDA-VA:1{FS:1-CCG:1} | AND | XF:23IDA-VA:1{FS:1-IP:1} | AND | XF:23IDA-VA:2{Mir:1-CCG:1} | AND | XF:23IDA-VA:2{Mir:1-IP:1} | AND | XF:23IDA-VA:1{FS:1-TCG:1} | AND | XF:23IDA-VA:2{Mir:1-TCG:1} | [8 empty] | ENABLE(XF:23IDA-VA:1{FS:1-GV:1}) | ENABLE(XF:23IDA-VA:1{FS:1-GV:2})
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(FE SHUTTER)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON FE) | [14 empty] | CLOSE(XF:23IDA-VA:1{FS:1-GV:1}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:2}) | CLOSE(XF:23IDA-VA:1{Mir:1-GV:1}) | CLOSE(XF:23IDA-VA:0{DP:1-GV:1})
NOT(BEAM ON FE) | AND | REQUEST CLOSE GV:1 | [16 empty] | CLOSE(XF:23IDA-VA:1{FS:1-GV:1})
NOT(BEAM ON FE) | AND | REQUEST CLOSE GV:2 | [16 empty] | CLOSE(XF:23IDA-VA:1{FS:1-GV:2})
XF:23IDA-VA:2{Mir:1-CCG:1} | AND | XF:23IDA-VA:2{Mir:1-IP:1} | AND | XF:23IDA:VA:1{SSh:1-CCG:1} | AND | XF:23IDA:VA:1{SSh:1-IP:1} | AND | XF:23ID1:VA{Diag:1-CCG:1} | AND | XF:23ID1:VA{Diag:1-IP:1} | AND | XF:23IDA-VA:2{Mir:1-TCG:1} | AND | XF:23IDA:VA:1{SSh:1-CCG:1} | AND | XF:23ID1:VA{Diag:1-CCG:1} |  |  | ENABLE(XF:23IDA-VA:2{Mir:1-GV:1})
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(FE SHUTTER)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON FE) | [14 empty] | CLOSE(XF:23IDA-VA:2{Mir:1-GV:1}) | CLOSE(XF:23IDA-VA:2{Mir:1-GV:2}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:1}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:2}) | CLOSE(XF:23IDA-VA:1{Mir:1-GV:1})
NOT(BEAM ON FE) | AND | REQUEST CLOSE GV:1 | [16 empty] | CLOSE(XF:23IDA-VA:2{Mir:1-GV:1})
XF:23IDA-VA:2{Mir:1-CCG:1} | AND | XF:23IDA-VA:2{Mir:1-IP:1} | AND | XF:23IDA:VA:2{SSh:1-CCG:1} | AND | XF:23IDA:VA:2{SSh:1-IP:1} | AND | XF:23ID2:VA{Diag:1-CCG:1} | AND | XF:23ID2:VA{Diag:1-IP:1} | AND | XF:23IDA-VA:2{Mir:1-TCG:1} | AND | XF:23IDA:VA:2{SSh:1-CCG:1} | AND | XF:23ID2:VA{Diag:1-CCG:1} |  |  | ENABLE(XF:23IDA-VA:2{Mir:1-GV:2})
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(FE SHUTTER)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON FE) | [14 empty] | CLOSE(XF:23IDA-VA:2{Mir:1-GV:1}) | CLOSE(XF:23IDA-VA:2{Mir:1-GV:2}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:1}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:2}) | CLOSE(XF:23IDA-VA:1{Mir:1-GV:1})
NOT(BEAM ON FE) | AND | REQUEST CLOSE GV:2 | [16 empty] | CLOSE(XF:23IDA-VA:2{Mir:1-GV:2})
23ID1 (CSX-1)
XF:23ID1-VA{Diag:01-CCG:1} | AND | XF:23ID1-VA{Diag:01-IP:1} | AND | XF:23IDA-VA:1{SSh:1-CCG:1} | AND | XF:23IDA-VA:1{SSh:1-IP:1} | AND | XF:23ID1-VA{Diag:02-CCG:1} | AND | XF:23ID1-VA{Diag:02-IP:1} | AND | XF:23ID1-VA{Diag:01-TCG:1} | AND | XF:23IDA-VA:1{SSh:1-TCG:1} | AND | XF:23ID1-VA{Diag:02-TCG:1} |  |  | ENABLE(XF:23ID1-VA{Diag:01-GV:1}
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | [12 empty] | CLOSE(FE SHUTTER)
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON FE) | [10 empty] | CLOSE(XF:23ID1-VA{Diag:01-GV:1} | CLOSE(XF:23IDA-VA:2{Mir:1-GV:1} | CLOSE(XF:23IDA-VA:2{Mir:1-GV:2} | CLOSE(XF:23IDA-VA:1{FS:1-GV:1}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:2})
NOT(BEAM ON 1) | AND | REQUEST CLOSE GV:1 | [16 empty] | CLOSE(XF:23ID1-VA{Diag:01-GV:1}
XF:23ID1-VA{Diag:02-CCG:1} | AND | XF:23ID1-VA{Diag:02-IP:1} | AND | XF:23ID1-VA{Mon-CCG:1} | AND | XF:23ID1-VA{Mon-IP:1} | AND | XF:23ID1-VA{Diag:02-TCG:1} | AND | XF:23ID1-VA{Mon-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{Diag:02-GV:1}
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(SHUTTER 1)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON 1) | [14 empty] | CLOSE(XF:23ID1-VA{Diag:02-GV:1} | CLOSE(XF:23ID1-VA{Diag:01-GV:1} | CLOSE(XF:23IDA-VA:2{Mir:1-GV:1}
NOT(BEAM ON 1) | AND | REQUEST CLOSE GV:1 | [16 empty] | CLOSE(XF:23ID1-VA{Diag:02-GV:1}
XF:23ID1-VA{Mon-CCG:1} | AND | XF:23ID1-VA{Mon-IP:1} | AND | XF:23ID1-VA{Slt:1-CCG:1} | AND | XF:23ID1-VA{Slt:1-IP:1} | AND | XF:23ID1-VA{Mon-TCG:1} | AND | XF:23ID1-VA{Slt:1-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{Mon-GV:1}
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(SHUTTER 1)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON 1) | [14 empty] | CLOSE(XF:23ID1-VA{Mon-GV:1} | CLOSE(XF:23ID1-VA{Diag:2-GV:1} | CLOSE(XF:23ID1-VA{Diag:1-GV:1}
NOT(BEAM ON 1) | AND | REQUEST CLOSE GV:1 | [16 empty] | CLOSE(XF:23ID1-VA{Mon-GV:1}
XF:23ID1-VA{Slt:1-CCG:1} | AND | XF:23ID1-VA{Slt:1-IP:1} | AND | XF:23ID1-VA{Mir:3-CCG:1} | AND | XF:23ID1-VA{Mir:3-IP:1} | AND | XF:23ID1-VA{Slt:1-TCG:1} | AND | XF:23ID1-VA{Mir:3-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{Slt:1-GV:1}
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(SHUTTER 1)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON 1) | [14 empty] | CLOSE(XF:23ID1-VA{Slt:1-GV:1} | CLOSE(XF:23ID1-VA{Mon-GV:1} | CLOSE(XF:23ID1-VA{Diag:2-GV:1}
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{Slt:1-GV:1}
XF:23ID1-VA{Mir:3-CCG:1} | AND | XF:23ID1-VA{Mir:3-IP:1} | AND | XF:23ID1-VA{Slt:2-CCG:1} | AND | XF:23ID1-VA{Slt:2-IP:1} | AND | XF:23ID1-VA{Diag:03-CCG:1} | AND | XF:23ID1-VA{Diag:03-IP:1} | AND | XF:23ID1-VA{Mir:3-TCG:1} | AND | XF:23ID1-VA{Slt:2-TCG:1} | AND | XF:23ID1-VA{Diag:03-TCG:1} |  |  | ENABLE(XF:23ID1-VA{Mir:3-GV:1})
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | [12 empty] | CLOSE(SHUTTER 1)
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON 1) | [10 empty] | CLOSE(XF:23ID1-VA{Mir:3-GV:1}) | CLOSE(XF:23ID1-VA{Slt:1-GV:1} | CLOSE(XF:23ID1-VA{Mon-GV:1}
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{Mir:3-GV:1})
XF:23ID1-VA{Diag:03-CCG:1} | AND | XF:23ID1-VA{Diag:03-IP:1} | AND | XF:23ID1-VA{SSh:2-CCG:1} | AND | XF:23ID1-VA{SSh:2-IP:1} | AND | XF:23ID1-VA{Diag:03-TCG:1} | AND | XF:23ID1-VA{SSh:2-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{Diag:03-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID1-VA{Diag:03-GV:1}) | CLOSE(XF:23ID1-VA{Mir:3-GV:1}) | CLOSE(XF:23ID1-VA{Slt:1-GV:1}
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{Diag:03-GV:1})
XF:23ID1-VA{SSh:2-CCG:1} | AND | XF:23ID1-VA{SSh:2-IP:1} | AND | XF:23ID1-VA{Diag:04-CCG:1} | AND | XF:23ID1-VA{Diag:04-IP:1} | AND | XF:23ID1-VA{SSh:2-TCG:1} | AND | XF:23ID1-VA{Diag:04-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{SSh:2-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID1-VA{SSh:2-GV:1}) | CLOSE(XF:23ID1-VA{Diag:03-GV:1}) | CLOSE(XF:23ID1-VA{Mir:3-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{SSh:2-GV:1})
XF:23ID1-VA{Diag:04-CCG:1} | AND | XF:23ID1-VA{Diag:04-IP:1} | AND | XF:23ID1-VA{SSh:2-CCG:1} | AND | XF:23ID1-VA{SSh:2-IP:1} | AND | XF:23ID1-VA{Diag:04-TCG:1} | AND | XF:23ID1-VA{SSh:2-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{Diag:04-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID1-VA{Diag:04-GV:1}) | CLOSE(XF:23ID1-VA{SSh:2-GV:1}) | CLOSE(XF:23ID1-VA{Diag:03-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{Diag:04-GV:1})
XF:23ID1-VA{DP:1-CCG:1} | AND | XF:23ID1-VA{DP:1-IP:1} | AND | XF:23ID1-VA{Diag:05-CCG:1} | AND | XF:23ID1-VA{Diag:05-IP:1} | AND | XF:23ID1-VA{DP:1-TCG:1} | AND | XF:23ID1-VA{Diag:05-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{DP:1-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID1-VA{DP:1-GV:1}) | CLOSE(XF:23ID1-VA{Diag:04-GV:1}) | CLOSE(XF:23ID1-VA{SSh:2-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{DP:1-GV:1})
XF:23ID1-VA{Diag:05-CCG:1} | AND | XF:23ID1-VA{Diag:05-IP:1} | AND | XF:23ID1-VA{Diag:06-CCG:1} | AND | XF:23ID1-VA{Diag:06-IP:1} | AND | XF:23ID1-VA{Diag:05-TCG:1} | AND | XF:23ID1-VA{Diag:06-TCG:1} | [8 empty] | ENABLE(XF:23ID1-VA{Diag:05-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID1-VA{Diag:05-GV:1}) | CLOSE(XF:23ID1-VA{DP:1-GV:1}) | CLOSE(XF:23ID1-VA{Diag:04-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{Diag:05-GV:1})
XF:23ID1-VA{Diag:06-CCG:1} | AND | XF:23ID1-VA{Diag:06-IP:1} | AND | ENDSTATION OK TO OPEN | AND | XF:23ID1-VA{Diag:06-TCG:1} | [12 empty] | ENABLE(XF:23ID1-VA{Diag:06-GV:1})
NOT(…) | OR | NOT(…) | OR | ENDSTATION VAC INTERLOCK NOT OK | OR | FAST VALVE TRIPPED | [12 empty] | CLOSE(XF:23ID1-VA{Diag:06-GV:1}) | CLOSE(XF:23ID1-VA{Diag:05-GV:1}) | CLOSE(XF:23ID1-VA{DP:1-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID1-VA{Diag:06-GV:1})
23ID2 (CSX-2)
XF:23IDA-VA:2{SSh:1-CCG:1} | AND | XF:23IDA-VA:2{SSh:1-IP:1} | AND | XF:23ID2-VA{Diag:1-CCG:1} | AND | XF:23ID2-VA{Diag:1-IP:1} | AND | XF:23ID2-VA{Mon:1-CCG:1} | AND | XF:23ID2-VA{Mon:1-IP:1} | AND | XF:23ID2-VA{Mon:1-TCG:1} | AND | XF:23IDA-VA:2{SSh:1-TCG:1} | AND | XF:23ID2-VA{Diag:1-TCG:1} |  |  | ENABLE(XF:23ID2-VA{Diag:01-GV:1})
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | [12 empty] | CLOSE(FE SHUTTER)
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON FE) | [10 empty] | CLOSE(XF:23ID2-VA{Diag:01-GV:1}) | CLOSE(XF:23IDA-VA:2{Mir:1-GV:2}) | CLOSE(XF:23IDA-VA:2{Mir:1-GV:1}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:1}) | CLOSE(XF:23IDA-VA:1{FS:1-GV:2})
REQUEST CLOSE GV:1 | AND | NOT(BEAM ON 2) | [16 empty] | CLOSE(XF:23ID2-VA{Diag:01-GV:1})
XF:23ID2-VA{Mon:1-CCG:1} | AND | XF:23ID2-VA{Mon:1-IP:1} | AND | XF:23ID2-VA{Slt:1-CCG:1} | AND | XF:23ID2-VA{Slt:1-IP:1} | AND | XF:23ID2-VA{Slt:1-TCG:1} | AND | XF:23ID2-VA{Mon:1-TCG:1} | [8 empty] | ENABLE(XF:23ID2-VA{Mon:1-GV:1})
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(SHUTTER 2)
NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON 2) | [14 empty] | CLOSE(XF:23ID2-VA{Mon:1-GV:1}) | CLOSE(XF:23ID2-VA{Diag:01-GV:1}) | CLOSE(XF:23IDA-VA:2{Mir:1-GV:2})
REQUEST CLOSE GV:1 | AND | NOT(BEAM ON 2) | [16 empty] | CLOSE(XF:23ID2-VA{Mon:1-GV:1})
XF:23ID2-VA{Slt:1-CCG:1} | AND | XF:23ID2-VA{Slt:1-IP:1} | AND | XF:23ID2-VA{SSh:2-CCG:1} | AND | XF:23ID2-VA{SSh:2-IP:1} | AND | XF:23ID2-VA{Pmp:Inl:01-CCG:1} | AND | XF:23ID2-VA{Pmp:Inl:01-IP:1} | AND | XF:23ID2-VA{Slt:1-TCG:1} | AND | XF:23ID2-VA{SSh:2-TCG:1} | AND | XF:23ID2-VA{Pmp:Inl:01-TCG:1} |  |  | ENABLE(XF:23ID2-VA{Slt:1-GV:1}) |  |  |  |  | CONTROLLED BY FAST VALVE
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(SHUTTER 2)
NOT(…) | OR | NOT(…) | [16 empty] | CLOSE(XF:23ID2-VA{Slt:1-GV:1}) | CLOSE(XF:23ID2-VA{Mon:1-GV:1}) | CLOSE(XF:23ID2-VA{Diag:01-GV:1})
REQUEST CLOSE GV:1 | AND | NOT(BEAM ON 2) | [16 empty] | CLOSE(XF:23ID2-VA{Slt:1-GV:1})
XF:23ID2-VA{SSh:2-CCG:1} | AND | XF:23ID2-VA{SSh:2-IP:1} | AND | XF:23ID2-VA{Pmp:Inl:01-CCG:1} | AND | XF:23ID2-VA{Pmp:Inl:01-IP:01} | AND | XF:23ID2-VA{Pmp:Inl:02-CCG:1} | AND | XF:23ID2-VA{Pmp:Inl:02-IP:01} | AND | XF:23ID2-VA{SSh:2-TCG:1} | AND | XF:23ID2-VA{Pmp:Inl:01-TCG:1} | AND | XF:23ID2-VA{Pmp:Inl:02-TCG:1} |  |  | ENABLE(XF:23ID2-VA{Pmp:Inl:01-GV:1}
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | [12 empty] | CLOSE(SHUTTER 2)
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | NOT(…) | AND | NOT(BEAM ON 2) | [10 empty] | CLOSE(XF:23ID2-VA{Pmp:Inl:01-GV:1} | CLOSE(XF:23ID2-VA{Slt:1-GV:1}) | CLOSE(XF:23ID2-VA{Mon:1-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Pmp:Inl:01-GV:1}
XF:23ID2-VA{Pmp:Inl:02-CCG:1} | AND | XF:23ID2-VA{Pmp:Inl:02-IP:01} | AND | XF:23ID2-VA{Pmp:Inl:03-CCG:1} | AND | XF:23ID2-VA{Pmp:Inl:03-IP:01} | AND | XF:23ID2-VA{Pmp:Inl:02-TCG:1} | AND | XF:23ID2-VA{Pmp:Inl:03-TCG:1} | [8 empty] | ENABLE(XF:23ID2-VA{Pmp:Inl:02-GV:1}
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID2-VA{Pmp:Inl:02-GV:1} | CLOSE(XF:23ID2-VA{Pmp:Inl:01-GV:1} | CLOSE(XF:23ID2-VA{Slt:1-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Pmp:Inl:02-GV:1}
XF:23ID2-VA{Pmp:Inl:03-CCG:1} | AND | XF:23ID2-VA{Pmp:Inl:03-IP:01} | AND | XF:23ID2-VA{Diag:02-CCG:1} | AND | XF:23ID2-VA{Diag:02-IP:1} | AND | XF:23ID2-VA{Pmp:Inl:03-TCG:1} | AND | XF:23ID2-VA{Diag:02-TCG:1} | [8 empty] | ENABLE(XF:23ID2-VA{Pmp:Inl:03-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID2-VA{Pmp:Inl:03-GV:1}) | CLOSE(XF:23ID2-VA{Pmp:Inl:02-GV:1} | CLOSE(XF:23ID2-VA{Pmp:Inl:01-GV:1}
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Pmp:Inl:03-GV:1})
XF:23ID2-VA{Diag:02-CCG:1} | AND | XF:23ID2-VA{Diag:02-IP:1} | AND | XF:23ID2-VA{Slt:2-CCG:1} | AND | XF:23ID2-VA{Slt:2-IP:01} | AND | XF:23ID2-VA{Diag:02-TCG:1} | AND | XF:23ID2-VA{Slt:2-TCG:1} | [8 empty] | ENABLE(XF:23ID2-VA{Diag:02-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID2-VA{Diag:02-GV:1}) | CLOSE(XF:23ID2-VA{Pmp:Inl:03-GV:1}) | CLOSE(XF:23ID2-VA{Pmp:Inl:02-GV:1}
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Diag:02-GV:1})
XF:23ID2-VA{Slt:2-CCG:1} | AND | XF:23ID2-VA{Slt:2-IP:01} | AND | XF:23ID2-VA{Chop-CCG:1} | AND | XF:23ID2-VA{Chop-IP:01} | AND | XF:23ID2-VA{Slt:2-TCG:1} | AND | XF:23ID2-VA{Chop-TCG:1} | [8 empty] | ENABLE(XF:23ID2-VA{Slt:2-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID2-VA{Slt:2-GV:1}) | CLOSE(XF:23ID2-VA{Diag:02-GV:1}) | CLOSE(XF:23ID2-VA{Pmp:Inl:03-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Slt:2-GV:1})
XF:23ID2-VA{Chop-CCG:1} | AND | XF:23ID2-VA{Chop-IP:01} | AND | XF:23ID2-VA{Slt:3-CCG:1} | AND | XF:23ID2-VA{Slt:3-IP:1} | AND | XF:23ID2-VA{GC-TCG:1} | AND | XF:23ID2-VA{Chop-TCG:1} | AND | XF:23ID2-VA{Slt:3-TCG:1} | [6 empty] | ENABLE(XF:23ID2-VA{Chop-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID2-VA{Chop-GV:1}) | CLOSE(XF:23ID2-VA{Slt:2-GV:1}) | CLOSE(XF:23ID2-VA{Diag:02-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Chop-GV:1})
XF:23ID2-VA{Slt:3-CCG:1} | AND | XF:23ID2-VA{Slt:3-IP:1} | AND | XF:23ID2-VA{GC-TCG:1} | AND | XF:23ID2-VA{Mir:3-CCG:1} | AND | XF:23ID2-VA{Mir:3-IP:1} | AND | XF:23ID2-VA{Slt:3-TCG:1} | AND | XF:23ID2-VA{Mir:3-TCG:1} | [6 empty] | ENABLE(XF:23ID2-VA{Slt:3-GV:1})
NOT(…) | OR | NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [12 empty] | CLOSE(XF:23ID2-VA{Slt:3-GV:1}) | CLOSE(XF:23ID2-VA{Chop-GV:1}) | CLOSE(XF:23ID2-VA{Slt:2-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Slt:3-GV:1})
XF:23ID2-VA{Mir:3-CCG:1} | AND | XF:23ID2-VA{Mir:3-IP:1} | AND | XF:23ID2-VA{Diag:03-CCG:1} | AND | XF:23ID2-VA{Diag:03-IP:1} | AND | XF:23ID2-VA{Mir:3-CCG:1} | AND | XF:23ID2-VA{Diag:03-CCG:1} | [8 empty] | ENABLE(XF:23ID2-VA{Mir:3-GV:1})
NOT(…) | OR | NOT(…) | OR | FAST VALVE TRIPPED | [14 empty] | CLOSE(XF:23ID2-VA{Mir:3-GV:1}) | CLOSE(XF:23ID2-VA{Slt:3-GV:1}) | CLOSE(XF:23ID2-VA{Chop-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Mir:3-GV:1})
XF:23ID2-VA{Diag:03-CCG:1} | AND | XF:23ID2-VA{Diag:03-IP:1} | AND | ENDSTATION OK TO OPEN | AND | XF:23ID2-VA{Diag:03-TCG:1} | [12 empty] | ENABLE(XF:23ID2-VA{Diag:03-GV:1})
NOT(…) | OR | NOT(…) | OR | ENDSTATION VAC INTERLOCK NOT OK | OR | FAST VALVE TRIPPED | [12 empty] | CLOSE(XF:23ID2-VA{Diag:03-GV:1}) | CLOSE(XF:23ID2-VA{Mir:3-GV:1}) | CLOSE(XF:23ID2-VA{Slt:3-GV:1})
REQUEST CLOSE GV:1 | [18 empty] | CLOSE(XF:23ID2-VA{Diag:03-GV:1})
23ID2 (CSX-2) GAS CELL LOGIC
CLOSED(XF:23ID2-VA{GC-GV:1}) | AND | CLOSED(XF:23ID2-VA{GC-GV:2}) | [16 empty] | ENABLE(XF:23ID2-VA{GC-GV:3})
OPEN(XF:23ID2-VA{GC-GV:1}) | OR | OPEN(XF:23ID2-VA{GC-GV:2}) | [16 empty] | CLOSE(XF:23ID2-VA{GC-GV:3})

## Vacuum Valve INterlock
The folowing valves if closed should not allow the FE shutter to be opened
XF:23IDA-VA:0{DP:1-GV:1}
XF:23IDA-VA:1{Mir:1-GV:1}
XF:23IDA-VA:1{FS:1-GV:1}
XF:23IDA-VA:2{Mir:1-GV:1}
XF:23IDA-VA:2{Mir:1-GV:2}
The folowing valves if closed should not allow the CSX-1 shutter to be opened
XF:23ID1-VA{Diag:01-GV:1}
XF:23ID1-VA{Diag:02-GV:1}
XF:23ID1-VA{Mon-GV:1}
The folowing valves if closed should not allow the CSX-2 shutter to be opened
XF:23ID2-VA{Diag:01-GV:1}
XF:23ID2-VA{Mon:1-GV:1}

## Water
Input | High SP | Low SP | Output | Action | Notes | DP Head | PPS Number | Nominal Flow (GPM) | MINOR ALM (GPM) | EPS TRIP (GPM)
XF:23IDA-VA:0{DP:1}F-I |  |  | FE Shutter | CLOSE |  | 2 |  | 0.5 | 0.425 | 0.25
XF:23IDA-OP:1{Mir:1}F-I |  |  | FE Shutter | CLOSE |  | 3 |  | 1.5 | 1.275 | 0.75
XF:23IDA-OP:1{Mir:1-Msk}F-I |  |  | FE Shutter | CLOSE |  | 4 |  | 1.5 | 1.275 | 0.75
XF:23IDA-OP:2{Mir:1A}F-I |  |  | FE Shutter | CLOSE |  | 8 |  | 0.8 | 0.68 | 0.4
XF:23IDA-OP:2{Mir:1-Msk}F-I |  |  | FE Shutter | CLOSE |  | 7 |  | 0.8 | 0.68 | 0.4
XF:23IDA-OP:1{FS:1}F-I |  |  | FE Shutter | CLOSE |  | 6 |  | 0.5 | 0.425 | 0.25
XF:23IDA-OP:2{Mir:1B}F-I |  |  | FE Shutter | CLOSE |  | 9 |  | 0.8 | 0.68 | 0.4
XF:23ID1-OP{Mon-Mir}F-I |  |  | Shutter 1 | CLOSE |  | 19 |  | 0.9 | 0.765 | 0.45
XF:23ID1-OP{Mon-Gtg}F-I |  |  | Shutter 1 | CLOSE |  | 20 |  | 0.5 | 0.425 | 0.25
XF:23ID1-OP{Diag:02}F-I |  |  | Shutter 1 | CLOSE |  | 21 |  | 0.3 | 0.255 | 0.15
XF:23ID2-OP{Mon-Mir}F-I |  |  | Shutter 2 | CLOSE |  | 15 |  | 0.9 | 0.765 | 0.45
XF:23ID2-OP{Mon-Gtg}F-I |  |  | Shutter 2 | CLOSE |  | 16 |  | 0.5 | 0.425 | 0.25
XF:23ID2-OP{Diag:01}F-I |  |  | Shutter 2 | CLOSE |  | 17 |  | 0.3 | 0.255 | 0.15
XF:23IDA-OP:0{Msk:1}F-I |  |  | PPS | PPS | In Series | 5 | 1 | 2.8 | 2.7
XF:23IDA-OP:1{Msk:1}F-I | [7 empty] | 0.75 | 0.7
XF:23IDA-OP:2{Msk:1}F-I | [5 empty] | 11 | 2 | 0.75 | 0.7
XF:23IDA-OP:1{SSh:1}F-I |  |  |  |  | In Series | 13 | 3 | 0.55 | 0.45
XF:23IDA-OP:2{SSh:1}F-I | [7 empty] | 0.55 | 0.45
XF:23ID1-OP{Mon-Msk}F-I | [5 empty] | 18 | 5
XF:23ID2-OP{Mon-Msk}F-I | [5 empty] | 14 | 4
[8 empty] | 0 | 0 | 0
[8 empty] | 0 | 0 | 0
XF:23IDA-UT{Circuit:1}F-I | [5 empty] | 1
XF:23IDA-UT{Circuit:10}F-I | [5 empty] | 10
mnigra | [5 empty] | Master
XF:23IDA-UT{DI}T:Supply-I | [5 empty] | DI RTD Supply | Slot 13 Ch 0
XF:23IDA-UT{DI}T:Return-I | [5 empty] | DI RTD Return | Slot 13 Ch 1
XF:23IDA-UT{PCW}T:Supply-I | [5 empty] | PCW RTD Supply | Slot 14 Ch 0
XF:23IDA-UT{PCW}T:Return-I | [5 empty] | PCW RTD Return | Slot 14 Ch 1
XF:23IDA-UT{DI}P:Supply-I | [5 empty] | DI Pressure Supply
XF:23IDA-UT{DI}P:Return-I | [5 empty] | DI Pressure Return
XF:23ID1-UT{DI}P:Supply-I | [5 empty] | DI Pressure Supply On Floor
XF:23ID1-UT{DI}P:Return-I | [5 empty] | DI Pressure Return On Floor
XF:23ID1-UT{PCW}P:Supply-I | [5 empty] | DI Pressure Supply On Floor
XF:23ID1-UT{PCW}P:Return-I | [5 empty] | DI Pressure Return On Floor

## VGC Controller Mapping
PV Name | Chan | Controller | Rack
XF:23IDA-VA:0{Diag:1-CCG:1} | 1 | {VGC:01} | RG:D2
XF:23IDA-VA:0{Msk:1-CCG:1} | 3 | {VGC:01} | RG:D2
XF:23IDA-VA:1{Mir:1-CCG:1} | 1 | {VGC:02} | RG:D2
XF:23IDA-VA:1{FS:1-CCG:1} | 3 | {VGC:02} | RG:D2
XF:23IDA-VA:2{Mir:1-CCG:1} | 1 | {VGC:03} | RG:D2
XF:23IDA-VA:1{SSh:1-CCG:1} | 3 | {VGC:03} | RG:D2
XF:23IDA-VA:2{SSh:1-CCG:1} | 3 | {VGC:04} | RG:D2
XF:23IDA-VA:0{Diag:1-TCG:1} | 5 | {VGC:01} | RG:D2
XF:23IDA-VA:0{Msk:1-TCG:1} | 6 | {VGC:01} | RG:D2
XF:23IDA-VA:1{Mir:1-TCG:1} | 5 | {VGC:02} | RG:D2
XF:23IDA-VA:1{FS:1-TCG:1} | 6 | {VGC:02} | RG:D2
XF:23IDA-VA:2{Mir:1-TCG:1} | 5 | {VGC:03} | RG:D2
XF:23IDA-VA:1{SSh:1-TCG:1} | 6 | {VGC:03} | RG:D2
XF:23IDA-VA:2{SSh:1-TCG:1} | 6 | {VGC:04} | RG:D2
XF:23ID1-VA{Diag:01-CCG:1} | 1 | {VGC:01} | RG:C1
XF:23ID1-VA{Diag:02-CCG:1} | 3 | {VGC:01} | RG:C1
XF:23ID1-VA{Mon-CCG:1} | 1 | {VGC:02} | RG:C1
XF:23ID1-VA{Slt:1-CCG:1} | 3 | {VGC:02} | RG:C1
XF:23ID1-VA{Mir:3-CCG:1} | 1 | {VGC:03} | RG:C1
XF:23ID1-VA{Slt:2-CCG:1} | 3 | {VGC:03} | RG:C1
XF:23ID1-VA{Diag:03-CCG:1} | 1 | {VGC:04} | RG:C1
XF:23ID1-VA{SSh:2-CCG:1} | 3 | {VGC:04} | RG:C1
XF:23ID1-VA{Diag:04-CCG:1} | 1 | {VGC:07} | RG:D1
XF:23ID1-VA{DP:1-CCG:1} | 3 | {VGC:07} | RG:D1
XF:23ID1-VA{Diag:05-CCG:1} | 1 | {VGC:08} | RG:D1
XF:23ID1-VA{Diag:06-CCG:1} | 3 | {VGC:08} | RG:D1
XF:23ID1-VA{Diag:01-TCG:1} | 5 | {VGC:01} | RG:C1
XF:23ID1-VA{Diag:02-TCG:1} | 6 | {VGC:01} | RG:C1
XF:23ID1-VA{Mon-TCG:1} | 5 | {VGC:02} | RG:C1
XF:23ID1-VA{Slt:1-TCG:1} | 6 | {VGC:02} | RG:C1
XF:23ID1-VA{Mir:3-TCG:1} | 5 | {VGC:03} | RG:C1
XF:23ID1-VA{Slt:2-TCG:1} | 6 | {VGC:03} | RG:C1
XF:23ID1-VA{Diag:03-TCG:1} | 5 | {VGC:04} | RG:C1
XF:23ID1-VA{SSh:2-TCG:1} | 6 | {VGC:04} | RG:C1
XF:23ID1-VA{Diag:04-TCG:1} | 5 | {VGC:07} | RG:D1
XF:23ID1-VA{DP:1-TCG:1} | 6 | {VGC:07} | RG:D1
XF:23ID1-VA{Diag:05-TCG:1} | 5 | {VGC:08} | RG:D1
XF:23ID1-VA{Diag:06-TCG:1} | 6 | {VGC:08} | RG:D1
XF:23ID2-VA{Diag:01-CCG:1} | 1 | {VGC:01} | RG:C2
XF:23ID2-VA{Mon-CCG:1} | 3 | {VGC:01} | RG:C2
XF:23ID2-VA{Slt:1-CCG:1} | 1 | {VGC:02} | RG:C2
XF:23ID2-VA{SSh:1-CCG:1} | 3 | {VGC:02} | RG:C2
XF:23ID2-VA{Pmp:Inl:01-CCG:1} | 1 | {VGC:03} | RG:C2
XF:23ID2-VA{Pmp:Inl:02-CCG:1} | 3 | {VGC:03} | RG:C2
XF:23ID2-VA{Pmp:Inl:03-CCG:1} | 1 | {VGC:04} | RG:C2
XF:23ID2-VA{Diag:02-CCG:1} | 3 | {VGC:04} | RG:C2
XF:23ID2-VA{Slt:2-CCG:1} | 1 | {VGC:05} | RG:C2
XF:23ID2-VA{Chop-CCG:1} | 3 | {VGC:05} | RG:C2
XF:23ID2-VA{Slt:3-CCG:1} | 1 | {VGC:06} | RG:C2
XF:23ID2-VA{GC-CCG:1} | 3 | {VGC:06} | RG:C2
XF:23ID2-VA{Mir:3-CCG:1} | 1 | {VGC:07} | RG:D2
XF:23ID2-VA{Diag:03-CCG:1} | 3 | {VGC:07} | RG:D2
XF:23ID2-VA{Diag:01-TCG:1} | 5 | {VGC:01} | RG:C2
XF:23ID2-VA{Mon-TCG:1} | 6 | {VGC:01} | RG:C2
XF:23ID2-VA{Slt:1-TCG:1} | 5 | {VGC:02} | RG:C2
XF:23ID2-VA{SSh:2-TCG:1} | 6 | {VGC:02} | RG:C2
XF:23ID2-VA{Pmp:Inl:01-TCG:1} | 5 | {VGC:03} | RG:C2
XF:23ID2-VA{Pmp:Inl:02-TCG:1} | 6 | {VGC:03} | RG:C2
XF:23ID2-VA{Pmp:Inl:03-TCG:1} | 5 | {VGC:04} | RG:C2
XF:23ID2-VA{Diag:02-TCG:1} | 6 | {VGC:04} | RG:C2
XF:23ID2-VA{Slt:2-TCG:1} | 5 | {VGC:05} | RG:C2
XF:23ID2-VA{Chop-TCG:1} | 6 | {VGC:05} | RG:C2
XF:23ID2-VA{Slt:3-TCG:1} | 5 | {VGC:06} | RG:C2
XF:23ID2-VA{GC-TCG:1} | 6 | {VGC:06} | RG:C2
XF:23ID2-VA{Mir:3-TCG:1} | 5 | {VGC:07} | RG:D2
XF:23ID2-VA{Diag:03-TCG:1} | 6 | {VGC:07} | RG:D2

## IPC Controller Mapping
EPICS PV | Chan | Controller | Rack
XF:23IDA-VA:0{Diag:1-IP:1} | 1 | IPC:01 | RG:B2
XF:23IDA-VA:0{Msk:1-IP:1} | 2 | IPC:01 | RG:B2
XF:23IDA-VA:0{DP:1-IP:1} | 1 | IPC:02 | RG:B2
XF:23IDA-VA:1{Mir:1-IP:1} | 2 | IPC:02 | RG:B2
XF:23IDA-VA:1{FS:1-IP:1} | 1 | IPC:03 | RG:B2
XF:23IDA-VA:2{Mir:1-IP:1} | 2 | IPC:03 | RG:B2
XF:23IDA-VA:1{SSh:1-IP:1} | 1 | IPC:04 | RG:B2
XF:23IDA-VA:2{SSh:1-IP:1} | 2 | IPC:04 | RG:B2
XF:23ID1-VA{Diag:01-IP:1} | 1 | IPC:01 | RG:C1
XF:23ID1-VA{Diag:02-IP:1} | 2 | IPC:01 | RG:C1
XF:23ID1-VA{Mon-IP:1} | 1 | IPC:02 | RG:C1
XF:23ID1-VA{Slt:1-IP:1} | 2 | IPC:02 | RG:C1
XF:23ID1-VA{Mir:3-IP:1} | 1 | IPC:03 | RG:C1
XF:23ID1-VA{Slt:2-IP:1} | 2 | IPC:03 | RG:C1
XF:23ID1-VA{Diag:03-IP:1} | 1 | IPC:04 | RG:C1
XF:23ID1-VA{SSh:2-IP:1} | 2 | IPC:04 | RG:C1
XF:23ID1-VA{Diag:04-IP:1} | 1 | IPC:07 | RG:D1
XF:23ID1-VA{DP:1-IP:1} | 2 | IPC:07 | RG:D1
XF:23ID1-VA{Diag:05-IP:1} | 1 | IPC:08 | RG:D1
XF:23ID1-VA{Diag:06-IP:1} | 2 | IPC:08 | RG:D1
XF:23ID2-VA{Diag:01-IP:1} | 1 | IPC:01 | RG:C2
XF:23ID2-VA{Mon-IP:1} | 2 | IPC:01 | RG:C2
XF:23ID2-VA{Slt:1-IP:1} | 1 | IPC:02 | RG:C2
XF:23ID2-VA{SSh:2-IP:1} | 2 | IPC:02 | RG:C2
XF:23ID2-VA{Pmp:Inl:01-IP:1} | 1 | IPC:03 | RG:C2
XF:23ID2-VA{Pmp:Inl:02-IP:1} | 2 | IPC:03 | RG:C2
XF:23ID2-VA{Pmp:Inl:03-IP:1} | 1 | IPC:04 | RG:C2
XF:23ID2-VA{Diag:02-IP:1} | 2 | IPC:04 | RG:C2
XF:23ID2-VA{Slt:2-IP:1} | NONE
XF:23ID2-VA{Chop-IP:1} | 1 | IPC:05 | RG:C2
XF:23ID2-VA{Slt:3-IP:1} | 2 | IPC:05 | RG:C2
XF:23ID2-VA{Mir:3-IP:1} | 1 | IPC:07 | RG:D2
XF:23ID2-VA{Diag:03-IP:1} | 2 | IPC:07 | RG:D2

## PPS
EPICS PV
Common Signals
XF:28ID-PPS{}Trip-Cmd
XF:23IDA-PPS{Hu}Secure-Sts
FE Shutter
XF:23ID-PPS{Sh:FE}Enbl-Sts
XF:23ID-PPS{Sh:FE}Cmd:Open-Cmd
XF:23ID-PPS{Sh:FE}Cmd:Close-Cmd
XF:23ID-PPS{Sh:FE}Sts:Open-Sts
Shutter 1 (In hutch A, 23-ID-1)
XF:23IDA-PPS:1{PSh}Enbl-Sts
XF:23IDA-PPS:1{PSh}Cmd:Open-Cmd
XF:23IDA-PPS:1{PSh}Cmd:Close-Cmd
XF:23IDA-PPS:1{PSh}Sts:Open-Sts
Shutter 2 (In hutch A, 23-ID-2)
XF:23IDA-PPS:2{PSh}Enbl-Sts
XF:23IDA-PPS:2{PSh}Cmd:Open-Cmd
XF:23IDA-PPS:2{PSh}Cmd:Close-Cmd
XF:23IDA-PPS:2{PSh}Sts:Open-Sts
Shutter 3 (Floor, 23-ID-1)
XF:23ID1-PPS{PSh}Enbl-Sts
XF:23ID1-PPS{PSh}Cmd:Open-Cmd
XF:23ID1-PPS{PSh}Cmd:Close-Cmd
XF:23ID1-PPS{PSh}Sts:Open-Sts
Shutter 4 (Floor, 23-ID-2)
XF:23ID2-PPS{PSh}Enbl-Sts
XF:23ID2-PPS{PSh}Cmd:Open-Cmd
XF:23ID2-PPS{PSh}Cmd:Close-Cmd
XF:23ID2-PPS{PSh}Sts:Open-Sts

## PLC EPS IO
Index | Component | Signal | Source | Pins | Destination | Pins | PLC Tag Name | Tag is Alias for: | Temp:emulation | Array element in Global tag | DINT used
1 | XF:23IDA-VA:0{Diag:1-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:0{IPC:01} J104 | 3, 1 | XF:23IDA-EPS{PLC:B2} J20 | 1, 6 | IDA_VA0_Diag1_IP1 | Local:2:I.Data.6 |  | IP_Sts_1[0] | 1
2 | XF:23IDA-VA:0{Msk:1-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:0{IPC:01} J104 | 6, 4 | XF:23IDA-EPS{PLC:B2} J20 | 2, 7 | IDA_VA0_Msk1_IP1 | Local:2:I.Data.7 | Local:1:I.Data.1 | IP_Sts_1[1]
3 | XF:23IDA-VA:0{DP:1-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:0{IPC:02} J104 | 3, 1 | XF:23IDA-EPS{PLC:B2} J21 | 1, 6 | IDA_VA0_DP1_IP1 | Local:2:I.Data.8 |  | IP_Sts_1[2]
4 | XF:23IDA-VA:1{Mir:1-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{IPC:02} J104 | 6, 4 | XF:23IDA-EPS{PLC:B2} J21 | 2, 7 | IDA_VA1_Mir1_IP1 | Local:2:I.Data.9 | Local:1:I.Data.2 | IP_Sts_1[3]
5 | XF:23IDA-VA:1{FS:1-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{IPC:03} J104 | 3, 1 | XF:23IDA-EPS{PLC:B2} J22 | 1, 6 | IDA_VA1_FS1_IP1 | Local:2:I.Data.10 | Local:1:I.Data.3 | IP_Sts_1[4]
6 | XF:23IDA-VA:2{Mir:1-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:2{IPC:03} J104 | 6, 4 | XF:23IDA-EPS{PLC:B2} J22 | 2, 7 | IDA_VA2_Mir1_IP1 | Local:2:I.Data.11 |  | IP_Sts_1[5]
7 | XF:23IDA-VA:1{PSh-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{IPC:04} J104 | 3, 1 | XF:23IDA-EPS{PLC:B2} J23 | 1, 6 | IDA_VA1_PSh_IP1 | Local:2:I.Data.12 | Local:1:I.Data.4 | IP_Sts_1[6]
8 | XF:23IDA-VA:2{PSh-IP:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:2{IPC:04} J104 | 3, 1 | XF:23IDA-EPS{PLC:B2} J23 | 2, 7 | IDA_VA2_PSh_IP1 | Local:2:I.Data.13 | Local:1:I.Data.5 | IP_Sts_1[7]
9 | XF:23ID1-VA{Diag:01-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:01} J104 | 3, 1 | XF:23ID1-EPS{PLC:C1} J20 | 1, 6 | ID1_VA_Diag01_IP1 | Vac_C1:1:I.6 | Local:1:I.Data.6 | IP_Sts_1[8]
10 | XF:23ID1-VA{Diag:02-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:01} J104 | 6, 4 | XF:23ID1-EPS{PLC:C1} J20 | 2, 7 | ID1_VA_Diag02_IP1 | Vac_C1:1:I.7 | Local:1:I.Data.7 | IP_Sts_1[9]
11 | XF:23ID1-VA{Mon-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:02} J104 | 3, 1 | XF:23ID1-EPS{PLC:C1} J21 | 1, 6 | ID1_VA_Mon_IP1 | Vac_C1:2:I.6 | Local:1:I.Data.8 | IP_Sts_1[10]
12 | XF:23ID1-VA{Slt:1-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:02} J104 | 6, 4 | XF:23ID1-EPS{PLC:C1} J21 | 2, 7 | ID1_VA_Slt1_IP1 | Vac_C1:2:I.7 | Local:1:I.Data.9 | IP_Sts_1[11]
13 | XF:23ID1-VA{Mir:3-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:03} J104 | 3, 1 | XF:23ID1-EPS{PLC:C1} J22 | 1, 6 | ID1_VA_Mir3_IP1 | Vac_C1:3:I.6 | Local:1:I.Data.10 | IP_Sts_1[12]
14 | XF:23ID1-VA{Slt:2-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:03} J104 | 6, 4 | XF:23ID1-EPS{PLC:C1} J22 | 2, 7 | ID1_VA_Slt2_IP1 | Vac_C1:3:I.7 |  | IP_Sts_1[13]
15 | XF:23ID1-VA{Diag:03-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:04} J104 | 3, 1 | XF:23ID1-EPS{PLC:C1} J23 | 1, 6 | ID1_VA_Diag03_IP1 | Vac_C1:4:I.6 |  | IP_Sts_1[14]
16 | XF:23ID1-VA{PSh-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:04} J104 | 6, 4 | XF:23ID1-EPS{PLC:C1} J23 | 2, 7 | ID1_VA_PSh_IP1 | Vac_C1:4:I.7 |  | IP_Sts_1[15]
17 | XF:23ID1-VA{Diag:04-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:07} J104 | 3, 1 | XF:23ID1-EPS{PLC:D1} J20 | 1, 6 | ID1_VA_Diag04_IP1 | Vac_D1:1:I.6 |  | IP_Sts_1[16]
18 | XF:23ID1-VA{DP:1-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:07} J104 | 6, 4 | XF:23ID1-EPS{PLC:D1} J20 | 2, 7 | ID1_VA_DP1_IP1 | Vac_D1:1:I.7 |  | IP_Sts_1[17]
19 | XF:23ID1-VA{Diag:05-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:08} J104 | 3, 1 | XF:23ID1-EPS{PLC:D1} J21 | 1, 6 | ID1_VA_Diag05_IP1 | Vac_D1:2:I.6 | Local:1:I.Data.11 | IP_Sts_1[18]
20 | XF:23ID1-VA{Diag:06-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{IPC:08} J104 | 6, 4 | XF:23ID1-EPS{PLC:D1} J21 | 2, 7 | ID1_VA_Diag06_IP1 | Vac_D1:2:I.7 | Local:1:I.Data.12 | IP_Sts_1[19]
21 | XF:23ID2-VA{Diag:01-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:01} J104 | 3, 1 | XF:23ID2-EPS{PLC:C2} J20 | 1, 6 | ID2_VA_Diag01_IP1 | Vac_C2:1:I.6 | Local:1:I.Data.13 | IP_Sts_1[20]
22 | XF:23ID2-VA{Mon-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:01} J104 | 6, 4 | XF:23ID2-EPS{PLC:C2} J20 | 2, 7 | ID2_VA_Mon_IP1 | Vac_C2:1:I.7 | Local:1:I.Data.14 | IP_Sts_1[21]
23 | XF:23ID2-VA{Slt:1-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:02} J104 | 3, 1 | XF:23ID2-EPS{PLC:C2} J21 | 1, 6 | ID2_VA_Slt1_IP1 | Vac_C2:2:I.6 |  | IP_Sts_1[22]
24 | XF:23ID2-VA{PSh-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:02} J104 | 6, 4 | XF:23ID2-EPS{PLC:C2} J21 | 2, 7 | ID2_VA_PSh_IP1 | Vac_C2:2:I.7 |  | IP_Sts_1[23]
25 | XF:23ID2-VA{Pmp:Inl:01-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:03} J104 | 3, 1 | XF:23ID2-EPS{PLC:C2} J22 | 1, 6 | ID2_VA_PmpInl01_IP1 | Vac_C2:3:I.6 | Local:1:I.Data.15 | IP_Sts_1[24]
26 | XF:23ID2-VA{Pmp:Inl:02-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:03} J104 | 6, 4 | XF:23ID2-EPS{PLC:C2} J22 | 2, 7 | ID2_VA_PmpInl02_IP1 | Vac_C2:3:I.7 | Local:1:I.Data.16 | IP_Sts_1[25]
27 | XF:23ID2-VA{Pmp:Inl:03-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:04} J104 | 3, 1 | XF:23ID2-EPS{PLC:C2} J23 | 1, 6 | ID2_VA_PmpInl03_IP1 | Vac_C2:4:I.6 | Local:1:I.Data.17 | IP_Sts_1[26]
28 | XF:23ID2-VA{Diag:02-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:04} J104 | 6, 4 | XF:23ID2-EPS{PLC:C2} J23 | 2, 7 | ID2_VA_Diag02_IP1 | Vac_C2:4:I.7 |  | IP_Sts_1[27]
29 | XF:23ID2-VA{Slt:2-IP:1} | Sts:Rly1PLC-Sts |  |  |  |  | ID2_VA_Slt2_IP1 | Vac_C2:6:I.6 |  | IP_Sts_1[28]
30 | XF:23ID2-VA{Chop-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:05} J104 | 3, 1 | XF:23ID2-EPS{PLC:C2} J24 | 1, 6 | ID2_VA_Chop_IP1 | Vac_C2:5:I.6 |  | IP_Sts_1[29]
31 | XF:23ID2-VA{Slt:3-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:05} J104 | 6, 4 | XF:23ID2-EPS{PLC:C2} J24 | 2, 7 | ID2_VA_Slt3_IP1 | Vac_C2:5:I.7 |  | IP_Sts_1[30]
32 | XF:23ID2-VA{Mir:3-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:07} J105 | 3, 1 | XF:23ID2-EPS{PLC:D2} J20 | 1, 6 | ID2_VA_Mir3_IP1 | Vac_D2:1:I.6 |  | IP_Sts_1[31]
33 | XF:23ID2-VA{Diag:03-IP:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{IPC:07} J106 | 6, 4 | XF:23ID2-EPS{PLC:D2} J20 | 2, 7 | ID2_VA_Diag03_IP1 | Vac_D2:1:I.7 |  | IP_Sts_2[0] | 1
34 |  |  | XF:23ID1-VA{IPC:09} J104 | 3, 1 | XF:23ID1-EPS{PLC:D1} J22 | 1, 6 | ID1_VA_Dif_IP1 | Vac_D1:3:I.6
35 |  |  | XF:23ID1-VA{IPC:09} J104 | 6, 4 | XF:23ID1-EPS{PLC:D1} J22 | 2, 7 | ID1_VA_Dif_IP2 | Vac_D1:3:I.7
36 | XF:23IDA-VA:0{Diag:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:0{VGC:01} RelOut | 1, 2 | XF:23IDA-EPS{PLC:B2} J11 | 1, 9 | IDA_VA0_Diag1_CCG1 | Local:1:I.Data.0 |  | CCG_Sts_1[0] | 1
37 | XF:23IDA-VA:0{Msk:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:0{VGC:01} RelOut | 9, 10 | XF:23IDA-EPS{PLC:B2} J11 | 3, 11 | IDA_VA0_Msk1_CCG1 | Local:1:I.Data.2 |  | CCG_Sts_1[1]
38 | XF:23IDA-VA:1{Mir:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{VGC:02} RelOut | 1, 2 | XF:23IDA-EPS{PLC:B2} J12 | 1, 9 | IDA_VA1_Mir1_CCG1 | Local:1:I.Data.6 |  | CCG_Sts_1[2]
39 | XF:23IDA-VA:1{FS:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{VGC:02} RelOut | 9, 10 | XF:23IDA-EPS{PLC:B2} J12 | 3, 11 | IDA_VA1_FS1_CCG1 | Local:1:I.Data.8 | Local:3:O.Data.0 | CCG_Sts_1[3]
40 | XF:23IDA-VA:2{Mir:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:2{VGC:03} RelOut | 1, 2 | XF:23IDA-EPS{PLC:B2} J13 | 1, 9 | IDA_VA2_Mir1_CCG1 | Local:1:I.Data.12 | Local:1:I.Data.18 | CCG_Sts_1[4]
41 | XF:23IDA-VA:1{PSh-CCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{VGC:03} RelOut | 9, 10 | XF:23IDA-EPS{PLC:B2} J13 | 3, 11 | IDA_VA1_PSh_CCG1 | Local:1:I.Data.14 | Local:1:I.Data.19 | CCG_Sts_1[5]
42 | XF:23IDA-VA:2{PSh-CCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:2{VGC:04} RelOut | 9, 10 | XF:23IDA-EPS{PLC:B2} J14 | 3, 11 | IDA_VA2_PSh_CCG1 | Local:1:I.Data.20 |  | CCG_Sts_1[6]
43 | XF:23ID1-VA{Diag:01-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:01} RelOut | 1, 2 | XF:23ID1-EPS{PLC:C1} J11 | 1, 9 | ID1_VA_Diag01_CCG1 | Vac_C1:1:I.0 |  | CCG_Sts_1[7]
44 | XF:23ID1-VA{Diag:02-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:01} RelOut | 9, 10 | XF:23ID1-EPS{PLC:C1} J11 | 3, 11 | ID1_VA_Diag02_CCG1 | Vac_C1:1:I.2 |  | CCG_Sts_1[8]
45 | XF:23ID1-VA{Mon-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:02} RelOut | 1, 2 | XF:23ID1-EPS{PLC:C1} J12 | 1, 9 | ID1_VA_Mon_CCG1 | Vac_C1:2:I.0 | Local:3:O.Data.1 | CCG_Sts_1[9]
46 | XF:23ID1-VA{Slt:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:02} RelOut | 9, 10 | XF:23ID1-EPS{PLC:C1} J12 | 3, 11 | ID1_VA_Slt1_CCG1 | Vac_C1:2:I.2 | Local:1:I.Data.23 | CCG_Sts_1[10]
47 | XF:23ID1-VA{Mir:3-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:03} RelOut | 1, 2 | XF:23ID1-EPS{PLC:C1} J13 | 1, 9 | ID1_VA_Mir3_CCG1 | Vac_C1:3:I.0 | Local:1:I.Data.24 | CCG_Sts_1[11]
48 | XF:23ID1-VA{Slt:2-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:03} RelOut | 9, 10 | XF:23ID1-EPS{PLC:C1} J13 | 3, 11 | ID1_VA_Slt2_CCG1 | Vac_C1:3:I.2 |  | CCG_Sts_1[12]
49 | XF:23ID1-VA{Diag:03-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:04} RelOut | 1, 2 | XF:23ID1-EPS{PLC:C1} J14 | 1, 9 | ID1_VA_Diag03_CCG1 | Vac_C1:4:I.0 | Local:1:I.Data.25 | CCG_Sts_1[13]
50 | XF:23ID1-VA{PSh-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:04} RelOut | 9, 10 | XF:23ID1-EPS{PLC:C1} J14 | 3, 11 | ID1_VA_PSh_CCG1 | Vac_C1:4:I.2 | Local:1:I.Data.26 | CCG_Sts_1[14]
51 | XF:23ID1-VA{Diag:04-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:07} RelOut | 1, 2 | XF:23ID1-EPS{PLC:D1} J11 | 1, 9 | ID1_VA_Diag04_CCG1 | Vac_D1:1:I.0 |  | CCG_Sts_1[15]
52 | XF:23ID1-VA{DP:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:07} RelOut | 9, 10 | XF:23ID1-EPS{PLC:D1} J11 | 3, 11 | ID1_VA_DP1_CCG1 | Vac_D1:1:I.2 |  | CCG_Sts_1[16]
53 | XF:23ID1-VA{Diag:05-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:08} RelOut | 1, 2 | XF:23ID1-EPS{PLC:D1} J12 | 1, 9 | ID1_VA_Diag05_CCG1 | Vac_D1:2:I.0 | Local:1:I.Data.27 | CCG_Sts_1[17]
54 | XF:23ID1-VA{Diag:06-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:08} RelOut | 9, 10 | XF:23ID1-EPS{PLC:D1} J12 | 3, 11 | ID1_VA_Diag06_CCG1 | Vac_D1:2:I.2 |  | CCG_Sts_1[18]
55 | XF:23ID2-VA{Diag:01-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:01} RelOut | 1, 2 | XF:23ID2-EPS{PLC:C2} J11 | 1, 9 | ID2_VA_Diag01_CCG1 | Vac_C2:1:I.0 |  | CCG_Sts_1[19]
56 | XF:23ID2-VA{Mon-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:01} RelOut | 9, 10 | XF:23ID2-EPS{PLC:C2} J11 | 3, 11 | ID2_VA_Mon_CCG1 | Vac_C2:1:I.2 | Local:2:I.Data.0 | CCG_Sts_1[20]
57 | XF:23ID2-VA{Slt:1-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:02} RelOut | 1, 2 | XF:23ID2-EPS{PLC:C2} J12 | 1, 9 | ID2_VA_Slt1_CCG1 | Vac_C2:2:I.0 |  | CCG_Sts_1[21]
58 | XF:23ID2-VA{PSh-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:02} RelOut | 9, 10 | XF:23ID2-EPS{PLC:C2} J12 | 3, 11 | ID2_VA_PSh_CCG1 | Vac_C2:2:I.2 |  | CCG_Sts_1[22]
59 | XF:23ID2-VA{Pmp:Inl:01-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:03} RelOut | 1, 2 | XF:23ID2-EPS{PLC:C2} J13 | 1, 9 | ID2_VA_PmpInl01_CCG1 | Vac_C2:3:I.0 |  | CCG_Sts_1[23]
60 | XF:23ID2-VA{Pmp:Inl:02-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:03} RelOut | 9, 10 | XF:23ID2-EPS{PLC:C2} J13 | 3, 11 | ID2_VA_PmpInl02_CCG1 | Vac_C2:3:I.2 | Local:3:O.Data.3 | CCG_Sts_1[24]
61 | XF:23ID2-VA{Pmp:Inl:03-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:04} RelOut | 1, 2 | XF:23ID2-EPS{PLC:C2} J14 | 1, 9 | ID2_VA_PmpInl03_CCG1 | Vac_C2:4:I.0 |  | CCG_Sts_1[25]
62 | XF:23ID2-VA{Diag:02-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:04} RelOut | 9, 10 | XF:23ID2-EPS{PLC:C2} J14 | 3, 11 | ID2_VA_Diag02_CCG1 | Vac_C2:4:I.2 |  | CCG_Sts_1[26]
63 | XF:23ID2-VA{Slt:2-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:05} RelOut | 1, 2 | XF:23ID2-EPS{PLC:C2} J15 | 1, 9 | ID2_VA_Slt2_CCG1 | Vac_C2:5:I.0 | Local:2:I.Data.1 | CCG_Sts_1[27]
64 | XF:23ID2-VA{Chop-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:05} RelOut | 9, 10 | XF:23ID2-EPS{PLC:C2} J15 | 3, 11 | ID2_VA_Chop_CCG1 | Vac_C2:5:I.2 | Local:2:I.Data.2 | CCG_Sts_1[28]
65 | XF:23ID2-VA{Slt:3-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:06} RelOut | 1, 2 | XF:23ID2-EPS{PLC:C2} J16 | 1, 9 | ID2_VA_Slt3_CCG1 | Vac_C2:6:I.0 | Local:2:I.Data.3 | CCG_Sts_1[29]
66 | XF:23ID2-VA{GC-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:06} RelOut | 9, 10 | XF:23ID2-EPS{PLC:C2} J16 | 3, 11 | ID2_VA_GC_CCG1 | Vac_C2:6:I.2 |  | CCG_Sts_1[30]
67 | XF:23ID2-VA{Mir:3-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:07} RelOut | 1, 2 | XF:23ID2-EPS{PLC:D2} J11 | 1, 9 | ID2_VA_Mir3_CCG1 | Vac_D2:1:I.0 |  | CCG_Sts_1[31]
68 | XF:23ID2-VA{Diag:03-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:07} RelOut | 9, 10 | XF:23ID2-EPS{PLC:D2} J11 | 3, 11 | ID2_VA_Diag03_CCG1 | Vac_D2:1:I.2 | Local:2:I.Data.4 | CCG_Sts_2[0] | 1
69 |  |  | XF:23ID1-VA{VGC:09} RelOut | 1, 2 | XF:23ID1-EPS{PLC:D1} J13 | 1, 9 | ID1_VA_Dif_CCG1 | Vac_D1:3:I.0 |  | CCG_Sts_2[1]
70 |  |  | XF:23ID1-VA{VGC:09} RelOut | 9, 10 | XF:23ID1-EPS{PLC:D1} J13 | 3, 11 | ID1_VA_DifLoadLck_CCG1 | Vac_D1:3:I.2 |  | CCG_Sts_2[2]
|  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 2 in rack) | 1, 2 | XF:23ID2-EPS{PLC:D2} J12 | 1, 9 | ID2_VA_CC_X_CCG1 | Vac_D2:2:I.0 |  | CCG_Sts_2[3]
|  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 2 in rack) | 9, 10 | XF:23ID2-EPS{PLC:D2} J12 | 3, 11 | ID2_VA_CC_I_CCG1 | Vac_D2:2:I.2 |  | CCG_Sts_2[4]
|  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 3 in rack) | 1, 2 | XF:23ID2-EPS{PLC:D2} J13 | 1, 9 | ID2_VA_IG_M_IG1 | Vac_D2:3:I.0 |  | CCG_Sts_2[5]
|  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 3 in rack) | 9, 10 | XF:23ID2-EPS{PLC:D2} J13 | 3, 11 | ID2_VA_IG_L_IG1 | Vac_D2:3:I.2 |  | CCG_Sts_2[6]
71 | XF:23IDA-VA:0{Diag:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:0{VGC:01} RelOut | 18, 19 | XF:23IDA-EPS{PLC:B2} J11 | 5, 13 | IDA_VA0_Diag1_TCG1 | Local:1:I.Data.4 |  | TCG_Sts_1[0] | 1
72 | XF:23IDA-VA:0{Msk:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:0{VGC:01} RelOut | 22, 23 | XF:23IDA-EPS{PLC:B2} J11 | 6, 14 | IDA_VA0_Msk1_TCG1 | Local:1:I.Data.5 | Local:1:I.Data.20 | TCG_Sts_1[1]
73 | XF:23IDA-VA:1{Mir:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{VGC:02} RelOut | 18, 19 | XF:23IDA-EPS{PLC:B2} J12 | 5, 13 | IDA_VA1_Mir1_TCG1 | Local:1:I.Data.10 |  | TCG_Sts_1[2]
74 | XF:23IDA-VA:1{FS:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{VGC:02} RelOut | 22, 23 | XF:23IDA-EPS{PLC:B2} J12 | 6, 14 | IDA_VA1_FS1_TCG1 | Local:1:I.Data.11 |  | TCG_Sts_1[3]
75 | XF:23IDA-VA:2{Mir:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:2{VGC:03} RelOut | 18, 19 | XF:23IDA-EPS{PLC:B2} J13 | 5, 13 | IDA_VA2_Mir1_TCG1 | Local:1:I.Data.16 | Local:1:I.Data.21 | TCG_Sts_1[4]
76 | XF:23IDA-VA:1{PSh-TCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:1{VGC:03} RelOut | 22, 23 | XF:23IDA-EPS{PLC:B2} J13 | 6, 14 | IDA_VA1_PSh_TCG1 | Local:1:I.Data.17 | Local:1:I.Data.22 | TCG_Sts_1[5]
77 | XF:23IDA-VA:2{PSh-TCG:1} | Sts:Rly1PLC-Sts | XF:23IDA-VA:2{VGC:04} RelOut | 22, 23 | XF:23IDA-EPS{PLC:B2} J14 | 6, 14 | IDA_VA2_PSh_TCG1 | Local:1:I.Data.23 |  | TCG_Sts_1[6]
78 | XF:23ID1-VA{Diag:01-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:01} RelOut | 18, 19 | XF:23ID1-EPS{PLC:C1} J11 | 5, 13 | ID1_VA_Diag01_TCG1 | Vac_C1:1:I.4 |  | TCG_Sts_1[7]
79 | XF:23ID1-VA{Diag:02-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:01} RelOut | 22, 23 | XF:23ID1-EPS{PLC:C1} J11 | 6, 14 | ID1_VA_Diag02_TCG1 | Vac_C1:1:I.5 |  | TCG_Sts_1[8]
80 | XF:23ID1-VA{Mon-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:02} RelOut | 18, 19 | XF:23ID1-EPS{PLC:C1} J12 | 5, 13 | ID1_VA_Mon_TCG1 | Vac_C1:2:I.4 |  | TCG_Sts_1[9]
81 | XF:23ID1-VA{Slt:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:02} RelOut | 22, 23 | XF:23ID1-EPS{PLC:C1} J12 | 6, 14 | ID1_VA_Slt1_TCG1 | Vac_C1:2:I.5 |  | TCG_Sts_1[10]
82 | XF:23ID1-VA{Mir:3-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:03} RelOut | 18, 19 | XF:23ID1-EPS{PLC:C1} J13 | 5, 13 | ID1_VA_Mir3_TCG1 | Vac_C1:3:I.4 | Local:3:O.Data.2 | TCG_Sts_1[11]
83 | XF:23ID1-VA{Slt:2-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:03} RelOut | 22, 23 | XF:23ID1-EPS{PLC:C1} J13 | 6, 14 | ID1_VA_Slt2_TCG1 | Vac_C1:3:I.5 | Local:1:I.Data.28 | TCG_Sts_1[12]
84 | XF:23ID1-VA{Diag:03-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:04} RelOut | 18, 19 | XF:23ID1-EPS{PLC:C1} J14 | 5, 13 | ID1_VA_Diag03_TCG1 | Vac_C1:4:I.4 |  | TCG_Sts_1[13]
85 | XF:23ID1-VA{PSh-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:04} RelOut | 22, 23 | XF:23ID1-EPS{PLC:C1} J14 | 6, 14 | ID1_VA_PSh_TCG1 | Vac_C1:4:I.5 |  | TCG_Sts_1[14]
86 | XF:23ID1-VA{Diag:04-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:07} RelOut | 18, 19 | XF:23ID1-EPS{PLC:D1} J11 | 5, 13 | ID1_VA_Diag04_TCG1 | Vac_D1:1:I.4 | Local:1:I.Data.29 | TCG_Sts_1[15]
87 | XF:23ID1-VA{DP:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:07} RelOut | 22, 23 | XF:23ID1-EPS{PLC:D1} J11 | 6, 14 | ID1_VA_DP1_TCG1 | Vac_D1:1:I.5 | Local:1:I.Data.30 | TCG_Sts_1[16]
88 | XF:23ID1-VA{Diag:05-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:07} RelOut | 18, 19 | XF:23ID1-EPS{PLC:D1} J11 | 5, 13 | ID1_VA_Diag05_TCG1 | Vac_D1:1:I.4 | Local:1:I.Data.31 | TCG_Sts_1[17]
89 | XF:23ID1-VA{Diag:06-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-VA{VGC:08} RelOut | 22, 23 | XF:23ID1-EPS{PLC:D1} J12 | 6, 14 | ID1_VA_Diag06_TCG1 | Vac_D1:2:I.5 |  | TCG_Sts_1[18]
90 | XF:23ID2-VA{Diag:01-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:01} RelOut | 18, 19 | XF:23ID2-EPS{PLC:C2} J11 | 5, 13 | ID2_VA_Diag01_TCG1 | Vac_C2:1:I.4 | Local:2:I.Data.5 | TCG_Sts_1[19]
91 | XF:23ID2-VA{Mon-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:01} RelOut | 22, 23 | XF:23ID2-EPS{PLC:C2} J11 | 6, 14 | ID2_VA_Mon_TCG1 | Vac_C2:1:I.5 |  | TCG_Sts_1[20]
92 | XF:23ID2-VA{Slt:1-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:02} RelOut | 18, 19 | XF:23ID2-EPS{PLC:C2} J12 | 5, 13 | ID2_VA_Slt1_TCG1 | Vac_C2:2:I.4 |  | TCG_Sts_1[21]
93 | XF:23ID2-VA{PSh-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:02} RelOut | 22, 23 | XF:23ID2-EPS{PLC:C2} J12 | 6, 14 | ID2_VA_PSh_TCG1 | Vac_C2:2:I.5 |  | TCG_Sts_1[22]
94 | XF:23ID2-VA{Pmp:Inl:01-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:03} RelOut | 18, 19 | XF:23ID2-EPS{PLC:C2} J13 | 5, 13 | ID2_VA_PmpInl01_TCG1 | Vac_C2:3:I.4 |  | TCG_Sts_1[23]
95 | XF:23ID2-VA{Pmp:Inl:02-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:03} RelOut | 22, 23 | XF:23ID2-EPS{PLC:C2} J13 | 6, 14 | ID2_VA_PmpInl02_TCG1 | Vac_C2:3:I.5 |  | TCG_Sts_1[24]
96 | XF:23ID2-VA{Pmp:Inl:03-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:04} RelOut | 18, 19 | XF:23ID2-EPS{PLC:C2} J14 | 5, 13 | ID2_VA_PmpInl03_TCG1 | Vac_C2:4:I.4 |  | TCG_Sts_1[25]
97 | XF:23ID2-VA{Diag:02-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:04} RelOut | 22, 23 | XF:23ID2-EPS{PLC:C2} J14 | 6, 14 | ID2_VA_Diag02_TCG1 | Vac_C2:4:I.5 |  | TCG_Sts_1[26]
98 | XF:23ID2-VA{Slt:2-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:05} RelOut | 18, 19 | XF:23ID2-EPS{PLC:C2} J15 | 5, 13 | ID2_VA_Slt2_TCG1 | Vac_C2:5:I.4 | Local:3:O.Data.4 | TCG_Sts_1[27]
99 | XF:23ID2-VA{Chop-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:05} RelOut | 22, 23 | XF:23ID2-EPS{PLC:C2} J15 | 6, 14 | ID2_VA_Chop_TCG1 | Vac_C2:5:I.5 | Local:2:I.Data.6 | TCG_Sts_1[28]
100 | XF:23ID2-VA{Slt:3-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:06} RelOut | 18, 19 | XF:23ID2-EPS{PLC:C2} J16 | 5, 13 | ID2_VA_Slt3_TCG1 | Vac_C2:6:I.4 | Local:2:I.Data.7 | TCG_Sts_1[29]
101 | XF:23ID2-VA{GC-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:06} RelOut | 22, 23 | XF:23ID2-EPS{PLC:C2} J16 | 6, 14 | ID2_VA_GC_TCG1 | Vac_C2:6:I.5 |  | TCG_Sts_1[30]
102 | XF:23ID2-VA{Mir:3-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:07} RelOut | 18, 19 | XF:23ID2-EPS{PLC:D2} J11 | 5, 13 | ID2_VA_Mir3_TCG1 | Vac_D2:1:I.4 |  | TCG_Sts_1[31]
103 | XF:23ID2-VA{Diag:03-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID2-VA{VGC:07} RelOut | 22, 23 | XF:23ID2-EPS{PLC:D2} J11 | 6, 14 | ID2_VA_Diag03_TCG1 | Vac_D2:1:I.5 | Local:2:I.Data.8 | TCG_Sts_2[0] | 1
104 |  |  | XF:23ID1-VA{VGC:09} RelOut | 18, 19 | XF:23ID1-EPS{PLC:D1} J13 | 5, 13 | ID1_VA_Dif_TCG1 | Vac_D1:3:I.4 |  | TCG_Sts_2[1]
105 |  |  | XF:23ID1-VA{VGC:09} RelOut | 22, 23 | XF:23ID1-EPS{PLC:D1} J13 | 6, 14 | ID1_VA_DifLoadLck_TCG1 | Vac_D1:3:I.5 |  | TCG_Sts_2[2]
106 |  |  |  | 1, 2 | XF:23ID1-EPS{PLC:D1} J14 | 1, 9 | ID1_VA_DifBacking_TCG1 | Vac_D1:4:I.0 |  | TCG_Sts_2[3]
107 |  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 2 in rack) | 1, 2 | XF:23ID2-EPS{PLC:D2} J12 | 5, 13 | ID2_VA_PG_X_TCG1 | Vac_D2:2:I.4 |  | TCG_Sts_2[4]
108 |  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 2 in rack) | 9, 10 | XF:23ID2-EPS{PLC:D2} J12 | 6, 14 | ID2_VA_PG_I_TCG1 | Vac_D2:2:I.5 |  | TCG_Sts_2[5]
109 |  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 3 in rack) | 1, 2 | XF:23ID2-EPS{PLC:D2} J13 | 5, 13 | ID2_VA_PG_M_TCG1 | Vac_D2:3:I.4 |  | TCG_Sts_2[6]
110 |  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 3 in rack) | 9, 10 | XF:23ID2-EPS{PLC:D2} J13 | 6, 14 | ID2_VA_PG_L_TCG1 | Vac_D2:3:I.5 |  | TCG_Sts_2[7]
111 |  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 4 in rack) | 1, 2 | XF:23ID2-EPS{PLC:D2} J14 | 5, 13 | ID2_VA_PG_B1_TCG1 | Vac_D2:4:I.4 |  | TCG_Sts_2[8]
112 |  |  | XF:23ID2-VA{VGC:??} RelOut (marked as 4 in rack) | 9, 10 | XF:23ID2-EPS{PLC:D2} J14 | 6, 14 | ID2_VA_PG_B2_TCG1 | Vac_D2:4:I.5 |  | TCG_Sts_2[9]
113 | XF:23IDA-VA:0{DP:1-GV:1} | Sw:OpnLim-Sts | XF:23IDA-VA:0{DP:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot1 | 0 | IDA_VA0_DP1_GV1_Opn | Drop_2:I.Data[1].0 |  | GV_01_Sts.OpnSw | 1
114 | XF:23IDA-VA:1{Mir:1-GV:1} | Sw:OpnLim-Sts | XF:23IDA-VA:1{Mir:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot1 | 2 | IDA_VA1_Mir1_GV1_Opn | Drop_2:I.Data[1].2 |  | GV_02_Sts.OpnSw | 1
115 | XF:23IDA-VA:1{FS:1-GV:1} | Sw:OpnLim-Sts | XF:23IDA-VA:1{FS:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot2 | 0 | IDA_VA1_FS1_GV1_Opn | Drop_2:I.Data[2].0 |  | GV_03_Sts.OpnSw | 1
116 | XF:23IDA-VA:1{FS:1-GV:2} | Sw:OpnLim-Sts | XF:23IDA-VA:1{FS:1-GV:2} |  | XF:23IDA-EPS{Drop:2} Slot2 | 2 | IDA_VA1_FS1_GV2_Opn | Drop_2:I.Data[2].2 |  | GV_04_Sts.OpnSw | 1
117 | XF:23IDA-VA:2{Mir:1-GV:1} | Sw:OpnLim-Sts | XF:23IDA-VA:2{Mir:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot1 | 4 | IDA_VA2_Mir1_GV1_Opn | Drop_2:I.Data[1].4 |  | GV_05_Sts.OpnSw | 1
118 | XF:23IDA-VA:2{Mir:1-GV:2} | Sw:OpnLim-Sts | XF:23IDA-VA:2{Mir:1-GV:2} |  | XF:23IDA-EPS{Drop:2} Slot1 | 6 | IDA_VA2_Mir1_GV2_Opn | Drop_2:I.Data[1].6 |  | GV_06_Sts.OpnSw | 1
119 | XF:23ID1-VA{Diag:01-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Diag:01-GV:1} |  | XF:23ID1-EPS{Armor:1} Ch0 | 4 | ID1_VA_Diag1_GV1_Opn | Armor_01:I.Data.0 |  | GV_07_Sts.OpnSw | 1
120 | XF:23ID1-VA{Diag:02-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Diag:02-GV:1} |  | XF:23ID1-EPS{Armor:2} Ch0 | 4 | ID1_VA_Diag2_GV1_Opn | Armor_02:I.Data.0 |  | GV_08_Sts.OpnSw | 1
121 | XF:23ID1-VA{Mon-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Mon-GV:1} |  | XF:23ID1-EPS{Drop:3} Slot1 | 0 | ID1_VA_Mon_GV1_Opn | Drop_3:I.Data[1].0 |  | GV_09_Sts.OpnSw | 1
122 | XF:23ID1-VA{Slt:1-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Slt:1-GV:1} |  | XF:23ID1-EPS{Armor:4} Ch0 | 4 | ID1_VA_Slt1_GV1_Opn | Armor_04:I.Data.0 |  | GV_10_Sts.OpnSw | 1
123 | XF:23ID1-VA{Mir:3-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Mir:3-GV:1} |  | XF:23ID1-EPS{Armor:4} Ch4 | 4 | ID1_VA_Mir3_GV1_Opn | Armor_04:I.Data.4 |  | GV_11_Sts.OpnSw | 1
124 | XF:23ID1-VA{FV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{FV:1} |  | XF:23ID1-EPS{Armor:6} Ch0 | 4 | ID1_VA_FV1_Opn | Armor_06:I.Data.0 |  | FV_01_Sts.OpnSw | 1
125 | XF:23ID1-VA{Diag:03-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Diag:03-GV:1} |  | XF:23ID1-EPS{Armor:7} Ch0 | 4 | ID1_VA_Diag03_GV1_Opn | Armor_07:I.Data.0 |  | GV_12_Sts.OpnSw | 1
126 | XF:23ID1-VA{PSh-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{PSh-GV:1} |  | XF:23ID1-EPS{Armor:8} Ch0 | 4 | ID1_VA_PSh_GV1_Opn | Armor_08:I.Data.0 |  | GV_13_Sts.OpnSw | 1
127 | XF:23ID1-VA{Diag:04-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Diag:04-GV:1} |  | XF:23ID1-EPS{Armor:9} Ch0 | 4 | ID1_VA_Diag04_GV1_Opn | Armor_09:I.Data.0 |  | GV_14_Sts.OpnSw | 1
128 | XF:23ID1-VA{DP:1-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{DP:1-GV:1} |  | XF:23ID1-EPS{Armor:10} Ch0 | 4 | ID1_VA_DP1_GV1_Opn | Armor_10:I.Data.0 |  | GV_15_Sts.OpnSw | 1
129 | XF:23ID1-VA{Diag:05-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Diag:05-GV:1} |  | XF:23ID1-EPS{Armor:11} Ch0 | 4 | ID1_VA_Diag05_GV1_Opn | Armor_11:I.Data.0 |  | GV_16_Sts.OpnSw | 1
130 | XF:23ID1-VA{Diag:06-GV:1} | Sw:OpnLim-Sts | XF:23ID1-VA{Diag:06-GV:1} |  | XF:23ID1-EPS{Armor:12} Ch0 | 4 | ID1_VA_Diag06_GV1_Opn | Armor_12:I.Data.0 |  | GV_17_Sts.OpnSw | 1
131 | XF:23ID2-VA{Diag:01-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Diag:01-GV:1} |  | XF:23ID2-EPS{Armor:1} Ch0 | 4 | ID2_VA_Diag01_GV1_Opn | Armor_13:I.Data.0 |  | GV_18_Sts.OpnSw | 1
132 | XF:23ID2-VA{Mon-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Mon-GV:1} |  | XF:23ID2-EPS{Drop:4} Slot1 | 0 | ID2_VA_Mon_GV1_Opn | Drop_4:I.Data[1].0 |  | GV_19_Sts.OpnSw | 1
133 | XF:23ID2-VA{Slt:1-GV:1} | Sw:OpnLim-Sts | Fast Valve Controller |  | Vacuum box |  | ID2_VA_Slt1_GV1_Opn | ID2_VA_FV_GV_Opn_Sts |  | GV_20_Sts.OpnSw | 1
134 | XF:23ID2-VA{FV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{FV:1} |  | XF:23ID2-EPS{Armor:3} Ch4 | 4 | ID2_VA_FV1_Opn | ID2_VA_FV_Vlv_Opn_Sts |  | FV_02_Sts.OpnSw | 1
135 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Pmp:Inl:01-GV:1} |  | XF:23ID2-EPS{Armor:4} Ch0 | 4 | ID2_VA_PmpInl01_GV1_Opn | Armor_16:I.Data.0 |  | GV_21_Sts.OpnSw | 1
136 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Pmp:Inl:02-GV:1} |  | XF:23ID2-EPS{Armor:5} Ch0 | 4 | ID2_VA_PmpInl02_GV1_Opn | Armor_17:I.Data.0 |  | GV_22_Sts.OpnSw | 1
137 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Pmp:Inl:03-GV:1} |  | XF:23ID2-EPS{Armor:6} Ch0 | 4 | ID2_VA_PmpInl03_GV1_Opn | Armor_18:I.Data.0 |  | GV_23_Sts.OpnSw | 1
138 | XF:23ID2-VA{Diag:02-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Diag:02-GV:1} |  | XF:23ID2-EPS{Armor:9} Ch0 | 4 | ID2_VA_Diag02_GV1_Opn | Armor_19:I.Data.0 |  | GV_24_Sts.OpnSw | 1
139 | XF:23ID2-VA{Slt:2-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Slt:2-GV:1} |  | XF:23ID2-EPS{Armor:9} Ch4 | 4 | ID2_VA_Slt2_GV1_Opn | Armor_19:I.Data.4 |  | GV_25_Sts.OpnSw | 1
140 | XF:23ID2-VA{Chop-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Chop-GV:1} |  | XF:23ID2-EPS{Armor:9} Ch8 | 4 | ID2_VA_Chop_GV1_Opn | Armor_19:I.Data.8 |  | GV_26_Sts.OpnSw | 1
141 | XF:23ID2-VA{Slt:3-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Slt:3-GV:1} |  | XF:23ID2-EPS{Armor:10} Ch0 | 4 | ID2_VA_Slt3_GV1_Opn | Armor_22:I.Data.0 |  | GV_27_Sts.OpnSw | 1
142 | XF:23ID2-VA{Mir:3-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Mir:3-GV:1} |  | XF:23ID2-EPS{Armor:10} Ch4 | 4 | ID2_VA_Mir3_GV1_Opn | Armor_22:I.Data.4 |  | GV_28_Sts.OpnSw | 1
143 | XF:23ID2-VA{Diag:03-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{Diag:03-GV:1} |  | XF:23ID2-EPS{Armor:11} Ch0 | 4 | ID2_VA_Diag03_GV1_Opn | Armor_23:I.Data.0 |  | GV_29_Sts.OpnSw | 1
144 | XF:23ID2-VA{GC-GV:1} | Sw:OpnLim-Sts | XF:23ID2-VA{GC-GV:1} |  | XF:23ID2-EPS{Armor:7} Ch0 | 4 | ID2_VA_GC_GV1_Opn | Armor_21:I.Data.0 |  | GV_30_Sts.OpnSw | 1
145 | XF:23ID2-VA{GC-GV:2} | Sw:OpnLim-Sts | XF:23ID2-VA{GC-GV:2} |  | XF:23ID2-EPS{Armor:7} Ch4 | 4 | ID2_VA_GC_GV2_Opn | Armor_21:I.Data.4 |  | GV_31_Sts.OpnSw | 1
146 | XF:23ID2-VA{GC-GV:3} | Sw:OpnLim-Sts | XF:23ID2-VA{GC-GV:3} |  | XF:23ID2-EPS{Armor:7} Ch8 | 4 | ID2_VA_GC_GV3_Opn | Armor_21:I.Data.8 |  | GV_32_Sts.OpnSw | 1
147 | XF:23IDA-VA:0{DP:1-GV:1} | Sw:ClsLim-Sts | XF:23IDA-VA:0{DP:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot1 | 1 | IDA_VA0_DP1_GV1_Cls | Drop_2:I.Data[1].1 |  | GV_01_Sts.ClsSw
148 | XF:23IDA-VA:1{Mir:1-GV:1} | Sw:ClsLim-Sts | XF:23IDA-VA:1{Mir:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot1 | 3 | IDA_VA1_Mir1_GV1_Cls | Drop_2:I.Data[1].3 |  | GV_02_Sts.ClsSw
149 | XF:23IDA-VA:1{FS:1-GV:1} | Sw:ClsLim-Sts | XF:23IDA-VA:1{FS:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot2 | 1 | IDA_VA1_FS1_GV1_Cls | Drop_2:I.Data[2].1 |  | GV_03_Sts.ClsSw
150 | XF:23IDA-VA:1{FS:1-GV:2} | Sw:ClsLim-Sts | XF:23IDA-VA:1{FS:1-GV:2} |  | XF:23IDA-EPS{Drop:2} Slot2 | 3 | IDA_VA1_FS1_GV2_Cls | Drop_2:I.Data[2].3 |  | GV_04_Sts.ClsSw
151 | XF:23IDA-VA:2{Mir:1-GV:1} | Sw:ClsLim-Sts | XF:23IDA-VA:2{Mir:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot1 | 5 | IDA_VA2_Mir1_GV1_Cls | Drop_2:I.Data[1].5 |  | GV_05_Sts.ClsSw
152 | XF:23IDA-VA:2{Mir:1-GV:2} | Sw:ClsLim-Sts | XF:23IDA-VA:2{Mir:1-GV:2} |  | XF:23IDA-EPS{Drop:2} Slot1 | 7 | IDA_VA2_Mir1_GV2_Cls | Drop_2:I.Data[1].7 |  | GV_06_Sts.ClsSw
153 | XF:23ID1-VA{Diag:01-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Diag:01-GV:1} |  | XF:23ID1-EPS{Armor:1} Ch1 | 2 | ID1_VA_Diag1_GV1_Cls | Armor_01:I.Data.1 |  | GV_07_Sts.ClsSw
154 | XF:23ID1-VA{Diag:02-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Diag:02-GV:1} |  | XF:23ID1-EPS{Armor:2} Ch1 | 2 | ID1_VA_Diag2_GV1_Cls | Armor_02:I.Data.1 |  | GV_08_Sts.ClsSw
155 | XF:23ID1-VA{Mon-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Mon-GV:1} |  | XF:23ID1-EPS{Drop:3} Slot1 | 1 | ID1_VA_Mon_GV1_Cls | Drop_3:I.Data[1].1 |  | GV_09_Sts.ClsSw
156 | XF:23ID1-VA{Slt:1-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Slt:1-GV:1} |  | XF:23ID1-EPS{Armor:4} Ch1 | 2 | ID1_VA_Slt1_GV1_Cls | Armor_04:I.Data.1 |  | GV_10_Sts.ClsSw
157 | XF:23ID1-VA{Mir:3-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Mir:3-GV:1} |  | XF:23ID1-EPS{Armor:4} Ch5 | 2 | ID1_VA_Mir3_GV1_Cls | Armor_04:I.Data.5 |  | GV_11_Sts.ClsSw
158 | XF:23ID1-VA{FV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{FV:1} |  | XF:23ID1-EPS{Armor:6} Ch1 | 2 | ID1_VA_FV1_Cls | Armor_06:I.Data.1 |  | FV_01_Sts.ClsSw
159 | XF:23ID1-VA{Diag:03-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Diag:03-GV:1} |  | XF:23ID1-EPS{Armor:7} Ch1 | 2 | ID1_VA_Diag03_GV1_Cls | Armor_07:I.Data.1 |  | GV_12_Sts.ClsSw
160 | XF:23ID1-VA{PSh-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{PSh-GV:1} |  | XF:23ID1-EPS{Armor:8} Ch1 | 2 | ID1_VA_PSh_GV1_Cls | Armor_08:I.Data.1 |  | GV_13_Sts.ClsSw
161 | XF:23ID1-VA{Diag:04-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Diag:04-GV:1} |  | XF:23ID1-EPS{Armor:9} Ch1 | 2 | ID1_VA_Diag04_GV1_Cls | Armor_09:I.Data.1 |  | GV_14_Sts.ClsSw
162 | XF:23ID1-VA{DP:1-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{DP:1-GV:1} |  | XF:23ID1-EPS{Armor:10} Ch1 | 2 | ID1_VA_DP1_GV1_Cls | Armor_10:I.Data.1 |  | GV_15_Sts.ClsSw
163 | XF:23ID1-VA{Diag:05-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Diag:05-GV:1} |  | XF:23ID1-EPS{Armor:11} Ch1 | 2 | ID1_VA_Diag05_GV1_Cls | Armor_11:I.Data.1 |  | GV_16_Sts.ClsSw
164 | XF:23ID1-VA{Diag:06-GV:1} | Sw:ClsLim-Sts | XF:23ID1-VA{Diag:06-GV:1} |  | XF:23ID1-EPS{Armor:12} Ch1 | 2 | ID1_VA_Diag06_GV1_Cls | Armor_12:I.Data.1 |  | GV_17_Sts.ClsSw
165 | XF:23ID2-VA{Diag:01-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Diag:01-GV:1} |  | XF:23ID2-EPS{Armor:1} Ch1 | 2 | ID2_VA_Diag01_GV1_Cls | Armor_13:I.Data.1 |  | GV_18_Sts.ClsSw
166 | XF:23ID2-VA{Mon-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Mon-GV:1} |  | XF:23ID2-EPS{Drop:4} Slot1 | 1 | ID2_VA_Mon_GV1_Cls | Drop_4:I.Data[1].1 |  | GV_19_Sts.ClsSw
167 | XF:23ID2-VA{Slt:1-GV:1} | Sw:ClsLim-Sts | Fast Valve Controller |  | Vacuum box |  | ID2_VA_Slt1_GV1_Cls | ID2_VA_FV_GV_Cls_Sts |  | GV_20_Sts.ClsSw
168 | XF:23ID2-VA{FV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{FV:1} |  | XF:23ID2-EPS{Armor:3} Ch5 | 2 | ID2_VA_FV1_Cls | ID2_VA_FV_Vlv_Cls_Sts |  | FV_02_Sts.ClsSw
169 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Pmp:Inl:01-GV:1} |  | XF:23ID2-EPS{Armor:4} Ch1 | 2 | ID2_VA_PmpInl01_GV1_Cls | Armor_16:I.Data.1 |  | GV_21_Sts.ClsSw
170 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Pmp:Inl:02-GV:1} |  | XF:23ID2-EPS{Armor:5} Ch1 | 2 | ID2_VA_PmpInl02_GV1_Cls | Armor_17:I.Data.1 |  | GV_22_Sts.ClsSw
171 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Pmp:Inl:03-GV:1} |  | XF:23ID2-EPS{Armor:6} Ch1 | 2 | ID2_VA_PmpInl03_GV1_Cls | Armor_18:I.Data.1 |  | GV_23_Sts.ClsSw
172 | XF:23ID2-VA{Diag:02-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Diag:02-GV:1} |  | XF:23ID2-EPS{Armor:9} Ch1 | 2 | ID2_VA_Diag02_GV1_Cls | Armor_19:I.Data.1 |  | GV_24_Sts.ClsSw
173 | XF:23ID2-VA{Slt:2-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Slt:2-GV:1} |  | XF:23ID2-EPS{Armor:9} Ch5 | 2 | ID2_VA_Slt2_GV1_Cls | Armor_19:I.Data.5 |  | GV_25_Sts.ClsSw
174 | XF:23ID2-VA{Chop-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Chop-GV:1} |  | XF:23ID2-EPS{Armor:9} Ch9 | 2 | ID2_VA_Chop_GV1_Cls | Armor_19:I.Data.9 |  | GV_26_Sts.ClsSw
175 | XF:23ID2-VA{Slt:3-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Slt:3-GV:1} |  | XF:23ID2-EPS{Armor:10} Ch1 | 2 | ID2_VA_Slt3_GV1_Cls | Armor_22:I.Data.1 |  | GV_27_Sts.ClsSw
176 | XF:23ID2-VA{Mir:3-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Mir:3-GV:1} |  | XF:23ID2-EPS{Armor:10} Ch5 | 2 | ID2_VA_Mir3_GV1_Cls | Armor_22:I.Data.5 |  | GV_28_Sts.ClsSw
177 | XF:23ID2-VA{Diag:03-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{Diag:03-GV:1} |  | XF:23ID2-EPS{Armor:11} Ch1 | 2 | ID2_VA_Diag03_GV1_Cls | Armor_23:I.Data.1 |  | GV_29_Sts.ClsSw
178 | XF:23ID2-VA{GC-GV:1} | Sw:ClsLim-Sts | XF:23ID2-VA{GC-GV:1} |  | XF:23ID2-EPS{Armor:7} Ch1 | 2 | ID2_VA_GC_GV1_Cls | Armor_21:I.Data.1 |  | GV_30_Sts.ClsSw
179 | XF:23ID2-VA{GC-GV:2} | Sw:ClsLim-Sts | XF:23ID2-VA{GC-GV:2} |  | XF:23ID2-EPS{Armor:7} Ch5 | 2 | ID2_VA_GC_GV2_Cls | Armor_21:I.Data.5 |  | GV_31_Sts.ClsSw
180 | XF:23ID2-VA{GC-GV:3} | Sw:ClsLim-Sts | XF:23ID2-VA{GC-GV:3} |  | XF:23ID2-EPS{Armor:7} Ch9 | 2 | ID2_VA_GC_GV3_Cls | Armor_21:I.Data.9 |  | GV_32_Sts.ClsSw
181 | XF:23IDA-VA:0{DP:1-GV:1} | Sts:Coil-Sts | XF:23IDA-VA:0{DP:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot9 | 0 | IDA_VA0_DP1_GV1_Coil | Drop_2:O.Data[9].0 |  | GV_01_Sts.Coil1
182 | XF:23IDA-VA:1{Mir:1-GV:1} | Sts:Coil-Sts | XF:23IDA-VA:1{Mir:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot9 | 3 | IDA_VA1_Mir1_GV1_Coil | Drop_2:O.Data[9].3 |  | GV_02_Sts.Coil1
183 | XF:23IDA-VA:1{FS:1-GV:1} | Sts:Coil-Sts | XF:23IDA-VA:1{FS:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot10 | 3 | IDA_VA1_FS1_GV1_Coil | Drop_2:O.Data[10].3 |  | GV_03_Sts.Coil1
184 | XF:23IDA-VA:1{FS:1-GV:2} | Sts:Coil-Sts | XF:23IDA-VA:1{FS:1-GV:2} |  | XF:23IDA-EPS{Drop:2} Slot10 | 5 | IDA_VA1_FS1_GV2_Coil | Drop_2:O.Data[10].5 |  | GV_04_Sts.Coil1
185 | XF:23IDA-VA:2{Mir:1-GV:1} | Sts:Coil-Sts | XF:23IDA-VA:2{Mir:1-GV:1} |  | XF:23IDA-EPS{Drop:2} Slot9 | 5 | IDA_VA2_Mir1_GV1_Coil | Drop_2:O.Data[9].5 |  | GV_05_Sts.Coil1
186 | XF:23IDA-VA:2{Mir:1-GV:2} | Sts:Coil-Sts | XF:23IDA-VA:2{Mir:1-GV:2} |  | XF:23IDA-EPS{Drop:2} Slot9 | 7 | IDA_VA2_Mir1_GV2_Coil | Drop_2:O.Data[9].7 |  | GV_06_Sts.Coil1
187 | XF:23ID1-VA{Diag:01-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Diag:01-GV:1} |  | XF:23ID1-EPS{Armor:1} Ch2 | 4 | ID1_VA_Diag1_GV1_Coil | Armor_01:O.Data.2 |  | GV_07_Sts.Coil1
188 | XF:23ID1-VA{Diag:02-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Diag:02-GV:1} |  | XF:23ID1-EPS{Armor:2} Ch2 | 4 | ID1_VA_Diag2_GV1_Coil | Armor_02:O.Data.2 |  | GV_08_Sts.Coil1
189 | XF:23ID1-VA{Mon-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Mon-GV:1} |  | XF:23ID1-EPS{Armor:2} Ch2 | 0 | ID1_VA_Mon_GV1_Coil | Drop_3:O.Data[4].0 |  | GV_09_Sts.Coil1
190 | XF:23ID1-VA{Slt:1-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Slt:1-GV:1} |  | XF:23ID1-EPS{Armor:4} Ch2 | 4 | ID1_VA_Slt1_GV1_Coil | Armor_04:O.Data.2 |  | GV_10_Sts.Coil1
191 | XF:23ID1-VA{Mir:3-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Mir:3-GV:1} |  | XF:23ID1-EPS{Armor:4} Ch6 | 4 | ID1_VA_Mir3_GV1_Coil | Armor_04:O.Data.6 |  | GV_11_Sts.Coil1
192 | XF:23ID1-VA{Diag:03-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Diag:03-GV:1} |  | XF:23ID1-EPS{Armor:7} Ch2 | 4 | ID1_VA_Diag03_GV1_Coil | Armor_07:O.Data.2 |  | GV_12_Sts.Coil1
193 | XF:23ID1-VA{PSh-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{PSh-GV:1} |  | XF:23ID1-EPS{Armor:8} Ch2 | 4 | ID1_VA_PSh_GV1_Coil | Armor_08:O.Data.2 |  | GV_13_Sts.Coil1
194 | XF:23ID1-VA{Diag:04-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Diag:04-GV:1} |  | XF:23ID1-EPS{Armor:9} Ch2 | 4 | ID1_VA_Diag04_GV1_Coil | Armor_09:O.Data.2 |  | GV_14_Sts.Coil1
195 | XF:23ID1-VA{DP:1-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{DP:1-GV:1} |  | XF:23ID1-EPS{Armor:10} Ch2 | 4 | ID1_VA_DP1_GV1_Coil | Armor_10:O.Data.2 |  | GV_15_Sts.Coil1
196 | XF:23ID1-VA{Diag:05-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Diag:05-GV:1} |  | XF:23ID1-EPS{Armor:11} Ch2 | 4 | ID1_VA_Diag05_GV1_Coil | Armor_11:O.Data.2 |  | GV_16_Sts.Coil1
197 | XF:23ID1-VA{Diag:06-GV:1} | Sts:Coil-Sts | XF:23ID1-VA{Diag:06-GV:1} |  | XF:23ID1-EPS{Armor:12} Ch2 | 4 | ID1_VA_Diag06_GV1_Coil | Armor_12:O.Data.2 |  | GV_17_Sts.Coil1
198 | XF:23ID2-VA{Diag:01-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Diag:01-GV:1} |  | XF:23ID2-EPS{Armor:1} Ch2 | 4 | ID2_VA_Diag01_GV1_Coil | Armor_13:O.Data.2 |  | GV_18_Sts.Coil1
199 | XF:23ID2-VA{Mon-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Mon-GV:1} |  | XF:23ID2-EPS{Drop:4} Slot4 | 0 | ID2_VA_Mon_GV1_Coil | Drop_4:O.Data[4].0 |  | GV_19_Sts.Coil1
200 | XF:23ID2-VA{Slt:1-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Slt:1-GV:1} |  | XF:23ID2-EPS{Armor:3} Ch2 | 4 | ID2_VA_Slt1_GV1_Coil | Armor_15:O.Data.2 |  | GV_20_Sts.Coil1
201 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Pmp:Inl:01-GV:1} |  | XF:23ID2-EPS{Armor:4} Ch2 | 4 | ID2_VA_PmpInl01_GV1_Coil | Armor_16:O.Data.2 |  | GV_21_Sts.Coil1
202 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Pmp:Inl:02-GV:1} |  | XF:23ID2-EPS{Armor:5} Ch2 | 4 | ID2_VA_PmpInl02_GV1_Coil | Armor_17:O.Data.2 |  | GV_22_Sts.Coil1
203 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Pmp:Inl:03-GV:1} |  | XF:23ID2-EPS{Armor:6} Ch2 | 4 | ID2_VA_PmpInl03_GV1_Coil | Armor_18:O.Data.2 |  | GV_23_Sts.Coil1
204 | XF:23ID2-VA{Diag:02-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Diag:02-GV:1} |  | XF:23ID2-EPS{Armor:7} Ch2 | 4 | ID2_VA_Diag02_GV1_Coil | Armor_19:O.Data.2 |  | GV_24_Sts.Coil1
205 | XF:23ID2-VA{Slt:2-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Slt:2-GV:1} |  | XF:23ID2-EPS{Armor:7} Ch6 | 4 | ID2_VA_Slt2_GV1_Coil | Armor_19:O.Data.6 |  | GV_25_Sts.Coil1
206 | XF:23ID2-VA{Chop-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Chop-GV:1} |  | XF:23ID2-EPS{Armor:7} Ch10 | 4 | ID2_VA_Chop_GV1_Coil | Armor_19:O.Data.10 |  | GV_26_Sts.Coil1
207 | XF:23ID2-VA{Slt:3-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Slt:3-GV:1} |  | XF:23ID2-EPS{Armor:10} Ch2 | 4 | ID2_VA_Slt3_GV1_Coil | Armor_22:O.Data.2 |  | GV_27_Sts.Coil1
208 | XF:23ID2-VA{Mir:3-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Mir:3-GV:1} |  | XF:23ID2-EPS{Armor:10} Ch6 | 4 | ID2_VA_Mir3_GV1_Coil | Armor_22:O.Data.6 |  | GV_28_Sts.Coil1
209 | XF:23ID2-VA{Diag:03-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{Diag:03-GV:1} |  | XF:23ID2-EPS{Armor:11} Ch2 | 4 | ID2_VA_Diag03_GV1_Coil | Armor_23:O.Data.2 |  | GV_29_Sts.Coil1
210 | XF:23ID2-VA{GC-GV:1} | Sts:Coil-Sts | XF:23ID2-VA{GC-GV:1} |  | XF:23ID2-EPS{Armor:9} Ch2 | 4 | ID2_VA_GC_GV1_Coil | Armor_21:O.Data.2 |  | GV_30_Sts.Coil1
211 | XF:23ID2-VA{GC-GV:2} | Sts:Coil-Sts | XF:23ID2-VA{GC-GV:2} |  | XF:23ID2-EPS{Armor:9} Ch6 | 4 | ID2_VA_GC_GV2_Coil | Armor_21:O.Data.6 |  | GV_31_Sts.Coil1
212 | XF:23ID2-VA{GC-GV:3} | Sts:Coil-Sts | XF:23ID2-VA{GC-GV:3} |  | XF:23ID2-EPS{Armor:9} Ch10 | 4 | ID2_VA_GC_GV3_Coil | Armor_21:O.Data.10 |  | GV_32_Sts.Coil1
213 | XF:23ID1-VA{FV-Vlv} | Rdy-Sts |  |  |  |  | ID1_VA_FV_Vlv_Rdy_Sts | Vac_D1:7:I.2 |  | FV_Sts[0]
214 | XF:23ID1-VA{FV-Vlv} | Intlk:Cls-Sts |  |  |  |  | ID1_VA_FV_Vlv_IntlkCls_Cmd | Vac_D1:O.Data[10].0 |  | FV_Sts[1]
215 | XF:23ID1-VA{FV-Vlv} | Intlk:Opn-Sts |  |  |  |  | ID1_VA_FV_Vlv_IntlkOpn_Cmd | Vac_D1:O.Data[10].1 |  | FV_Sts[2]
216 | XF:23ID1-VA{FV-Vlv} | Cls-Sts |  |  |  |  | ID1_VA_FV_Vlv_Cls_Sts | Vac_D1:7:I.1 |  | FV_Sts[3]
217 | XF:23ID1-VA{FV-Vlv} | Opn-Sts |  |  |  |  | ID1_VA_FV_Vlv_Opn_Sts | Vac_D1:7:I.0 |  | FV_Sts[4]
218 | XF:23ID1-VA{FV-GV} | Intlk:Cls-Sts |  |  |  |  | ID1_VA_FV_GV_IntlkCls_Cmd | Vac_D1:O.Data[10].3 |  | FV_Sts[5]
219 | XF:23ID1-VA{FV-GV} | Intlk:Opn-Sts |  |  |  |  | ID1_VA_FV_GV_IntlkOpn_Cmd | Vac_D1:O.Data[10].4 |  | FV_Sts[6]
220 | XF:23ID1-VA{FV-GV} | Opn-Sts |  |  |  |  | ID1_VA_FV_GV_Opn_Sts | Vac_D1:8:I.0 |  | FV_Sts[7]
221 | XF:23ID1-VA{FV-GV} | Rdy-Sts |  |  |  |  | ID1_VA_FV_GV_Rdy_Sts | Vac_D1:8:I.2 |  | FV_Sts[8]
222 | XF:23ID1-VA{FV-GV} | Cls-Sts |  |  |  |  | ID1_VA_FV_GV_Cls_Sts | Vac_D1:8:I.1 |  | FV_Sts[9]
223 | XF:23ID1-VA{FV-GV} | Opn-Sts |  |  |  |  | ID1_VA_FV_GV_Opn_Sts | Vac_D1:O.Data[10].5 |  | FV_Sts[10]
224 | XF:23ID1-VA{FV-GV} | Cmd:Cls-Sts |  |  |  |  | ID1_VA_FV_GV_Cls_Sts | Vac_D1:O.Data[10].6 |  | FV_Sts[11]
225 | XF:23ID2-VA{FV-Vlv} | Cmd:Rdy-Sts |  |  |  |  | ID2_VA_FV_Vlv_Rdy_Sts | Vac_D2:7:I.2 |  | FV_Sts[12]
226 | XF:23ID2-VA{FV-Vlv} | Intlk:Cls-Sts |  |  |  |  | ID2_VA_FV_Vlv_IntlkCls_Cmd | Vac_D2:O.Data[10].0 |  | FV_Sts[13]
227 | XF:23ID2-VA{FV-Vlv} | Intlk:Opn-Sts |  |  |  |  | ID2_VA_FV_Vlv_IntlkOpn_Cmd | Vac_D2:O.Data[10].1 |  | FV_Sts[14]
228 | XF:23ID2-VA{FV-Vlv} | Cls-Sts |  |  |  |  | ID2_VA_FV_Vlv_Cls_Sts | Vac_D2:7:I.1 |  | FV_Sts[15]
229 | XF:23ID2-VA{FV-Vlv} | Opn-Sts |  |  |  |  | ID2_VA_FV_Vlv_Opn_Sts | Vac_D2:7:I.0 |  | FV_Sts[16]
230 | XF:23ID2-VA{FV-GV} | Intlk:Cls-Sts |  |  |  |  | ID2_VA_FV_GV_IntlkCls_Cmd | Vac_D2:O.Data[10].3 |  | FV_Sts[17]
231 | XF:23ID2-VA{FV-GV} | Intlk:Opn-Sts |  |  |  |  | ID2_VA_FV_GV_IntlkOpn_Cmd | Vac_D2:O.Data[10].4 |  | FV_Sts[18]
232 | XF:23ID2-VA{FV-GV} | Opn-Sts |  |  |  |  | ID2_VA_FV_GV_Opn_Sts | Vac_D2:8:I.0 |  | FV_Sts[19]
233 | XF:23ID2-VA{FV-GV} | Rdy-Sts |  |  |  |  | ID2_VA_FV_GV_Rdy_Sts | Vac_D2:8:I.2 |  | FV_Sts[20]
234 | XF:23ID2-VA{FV-GV} | Cls-Sts |  |  |  |  | ID2_VA_FV_GV_Cls_Sts | Vac_D2:8:I.1 |  | FV_Sts[21]
235 | XF:23ID2-VA{FV-GV} | Cmd:Opn-Sts |  |  |  |  | ID2_VA_FV_GV_Opn_Cmd | Vac_D2:O.Data[10].5 |  | FV_Sts[22]
236 | XF:23ID2-VA{FV-GV} | Cmd:Cls-Sts |  |  |  |  | ID2_VA_FV_GV_Cls_Cmd | Vac_D2:O.Data[10].6 |  | FV_Sts[23]
225 | XF:23IDA-CT{PLC:BL}Out:VaFE-Sts | [5 empty] | Vac_Sts_to_FE | Drop_2:O.Data[17].0 |  | Misc_Sts[0] | 1
226 | XF:23IDA-CT{PLC:BL}Out:VaES-Sts | [5 empty] | Vac_Sts_to_ES | Armor_F1:O.Data.1 |  | Misc_Sts[1]
227 | XF:23IDA-CT{PLC:BL}In:VaFE-Sts | [5 empty] | Vac_Sts_from_FE | Drop_2:7:I.0 |  | Misc_Sts[2]
228 | XF:23IDA-CT{PLC:BL}In:VaES-Sts | [5 empty] | Vac_Sts_from_ES | Armor_F1:I.Data.0 |  | Misc_Sts[3]
229 | XF:23IDA-CT{PLC:BL}Out:VaES2-Sts | [5 empty] | Vac_Sts_to_ES2 | Spare_Unused:O.Data.1 |  | Misc_Sts[4]
230 | XF:23IDA-CT{PLC:BL}In:VaES2-Sts | [5 empty] | Vac_Sts_from_ES2 | Spare_Unused:I.Data.0 |  | Misc_Sts[5]
231 | XF:23ID-EPS{} | Out:EPS_Permit-Sts |  |  |  |  | USER_INTERLOCK | Drop_2:O.Data[12].5 |  | Misc_Sts[6]
232 | XF:23ID-PPS{Sh:FE} | Enbl-Sts |  |  |  |  | FE_SH_ENABLE_Sts | Drop_2:3:I.0 |  | SH_FE_Sts.EnableRaw
233 | XF:23ID-PPS{Sh:FE} | Sts:Pos-Sts |  |  |  |  | FE_SH_CLOSED_Sts | Drop_2:3:I.1 |  | SH_FE_Sts.StatusRaw
234 | XF:23ID-PPS{Sh:FE} | Sts:OpnCmd-Sts |  |  |  |  | FE_SH_CMD_Sts | Drop_2:3:I.2 |  | SH_FE_Sts.CMDRaw
235 | XF:23ID-PPS{Sh:FE} | Cmd:Open-Sts |  |  |  |  | FE_SH_OPEN_Cmd | Drop_2:O.Data[12].3 |  | SH_FE_Sts.OpenRaw
236 | XF:23ID-PPS{Sh:FE} | Cmd:Close-Sts |  |  |  |  | FE_SH_CLOSE_Cmd | Drop_2:O.Data[12].4 |  | SH_FE_Sts.CloseRaw
237 | XF:23IDA-PPS:1{PSh} | Enbl-Sts |  |  |  |  | PSH_1_ENABLE_Sts | Drop_2:3:I.3 |  | PSH_1_Sts.EnableRaw
238 | XF:23IDA-PPS:1{PSh} | Sts:Pos-Sts |  |  |  |  | PSH_1_CLOSED_Sts | Drop_2:3:I.4 |  | PSH_1_Sts.StatusRaw
239 | XF:23IDA-PPS:1{PSh} | Sts:OpnCmd-Sts |  |  |  |  | PSH_1_CMD_Sts | Drop_2:3:I.5 |  | PSH_1_Sts.CMDRaw
240 | XF:23IDA-PPS:1{PSh} | Cmd:Open-Sts |  |  |  |  | PSH_1_OPEN_Cmd | Drop_2:O.Data[12].6 |  | PSH_1_Sts.OpenRaw
241 | XF:23IDA-PPS:1{PSh} | Cmd:Close-Sts |  |  |  |  | PSH_1_CLOSE_Cmd | Drop_2:O.Data[11].0 |  | PSH_1_Sts.CloseRaw
242 | XF:23IDA-PPS:2{PSh} | Enbl-Sts |  |  |  |  | PSH_2_ENABLE_Sts | Drop_2:4:I.1 |  | PSH_2_Sts.EnableRaw
243 | XF:23IDA-PPS:2{PSh} | Sts:Pos-Sts |  |  |  |  | PSH_2_CLOSED_Sts | Drop_2:4:I.2 |  | PSH_2_Sts.StatusRaw
244 | XF:23IDA-PPS:2{PSh} | Sts:OpnCmd-Sts |  |  |  |  | PSH_2_CMD_Sts | Drop_2:4:I.3 |  | PSH_2_Sts.CMDRaw
245 | XF:23IDA-PPS:2{PSh} | Cmd:Open-Sts |  |  |  |  | PSH_2_OPEN_Cmd | Drop_2:O.Data[11].3 |  | PSH_2_Sts.OpenRaw
246 | XF:23IDA-PPS:2{PSh} | Cmd:Close-Sts |  |  |  |  | PSH_2_CLOSE_Cmd | Drop_2:O.Data[11].4 |  | PSH_2_Sts.CloseRaw
247 | XF:23ID1-PPS{PSh} | Enbl-Sts |  |  |  |  | PSH_3_ENABLE_Sts | Drop_2:3:I.6 |  | PSH_3_Sts.EnableRaw
248 | XF:23ID1-PPS{PSh} | Sts:Pos-Sts |  |  |  |  | PSH_3_CLOSED_Sts | Drop_2:3:I.7 |  | PSH_3_Sts.StatusRaw
249 | XF:23ID1-PPS{PSh} | Sts:OpnCmd-Sts |  |  |  |  | PSH_3_CMD_Sts | Drop_2:4:I.0 |  | PSH_3_Sts.CMDRaw
250 | XF:23ID1-PPS{PSh} | Cmd:Open-Sts |  |  |  |  | PSH_3_OPEN_Cmd | Drop_2:O.Data[11].1 |  | PSH_3_Sts.OpenRaw
251 | XF:23ID1-PPS{PSh} | Cmd:Close-Sts |  |  |  |  | PSH_3_CLOSE_Cmd | Drop_2:O.Data[11].2 |  | PSH_3_Sts.CloseRaw
252 | XF:23ID2-PPS{PSh} | Enbl-Sts |  |  |  |  | PSH_4_ENABLE_Sts | Drop_2:4:I.4 |  | PSH_4_Sts.EnableRaw
253 | XF:23ID2-PPS{PSh} | Sts:Pos-Sts |  |  |  |  | PSH_4_CLOSED_Sts | Drop_2:4:I.5 |  | PSH_4_Sts.StatusRaw
254 | XF:23ID2-PPS{PSh} | Sts:OpnCmd-Sts |  |  |  |  | PSH_4_CMD_Sts | Drop_2:4:I.6 |  | PSH_4_Sts.CMDRaw
255 | XF:23ID2-PPS{PSh} | Cmd:Open-Sts |  |  |  |  | PSH_4_OPEN_Cmd | Drop_2:O.Data[11].5 |  | PSH_4_Sts.OpenRaw
256 | XF:23ID2-PPS{PSh} | Cmd:Close-Sts |  |  |  |  | PSH_4_CLOSE_Cmd | Drop_2:O.Data[11].6 |  | PSH_4_Sts.CloseRaw
257 | XF:23IDA-OP:0{Msk:1} | T:1-I |  |  | Slot 10 Ch 0 |  | IDA_OP0_Msk1_T1 | Drop_1:10:I.Ch0Data | Local:2:I.Data.9 | IDA_T_I[0] | 1
258 | XF:23IDA-OP:0{Msk:1} | T:2-I |  |  | Slot 10 Ch 1 |  | IDA_OP0_Msk1_T2 | Drop_1:10:I.Ch1Data | Local:2:I.Data.10 | IDA_T_I[1] | 1
261 | XF:23IDA-OP:1{Mir:1-Msk} | T:1-I |  |  | Slot 2 Ch 0 |  | IDA_OP1_Mir1_Msk_T1 | Drop_1:2:I.Ch0Data |  | IDA_T_I[2] | 1
262 | XF:23IDA-OP:1{Mir:1-Msk} | T:2-I |  |  | Slot 2 Ch 1 |  | IDA_OP1_Mir1_Msk_T2 | Drop_1:2:I.Ch1Data |  | IDA_T_I[3] | 1
263 | XF:23IDA-OP:1{Mir:1} | T:1-I |  |  | Slot 1 Ch 0 |  | IDA_OP1_Mir1_T1 | Drop_1:1:I.Ch0Data | Local:2:I.Data.11 | IDA_T_I[4] | 1
264 | XF:23IDA-OP:1{Mir:1} | T:2-I |  |  | Slot 1 Ch 1 |  | IDA_OP1_Mir1_T2 | Drop_1:1:I.Ch1Data | Local:2:I.Data.12 | IDA_T_I[5] | 1
265 | XF:23IDA-OP:1{Msk:1} | T:1-I |  |  | Slot 11 Ch 0 |  | IDA_OP1_Msk1_T1 | Drop_1:11:I.Ch0Data | Local:2:I.Data.13 | IDA_T_I[6] | 1
266 | XF:23IDA-OP:1{Msk:1} | T:2-I |  |  | Slot 11 Ch 1 |  | IDA_OP1_Msk1_T2 | Drop_1:11:I.Ch1Data |  | IDA_T_I[7] | 1
267 | XF:23IDA-OP:1{FS:1} | T-I |  |  | Slot 3 Ch 0 |  | IDA_OP1_FS1_T | Drop_1:3:I.Ch0Data |  | IDA_T_I[8] | 1
268 | XF:23IDA-OP:2{Mir:1A-Msk} | T:1-I |  |  | Slot 4 Ch 1 |  | IDA_OP2_Mir1A_Msk_T1 | Drop_1:4:I.Ch1Data |  | IDA_T_I[9] | 1
269 | XF:23IDA-OP:2{Mir:1B-Msk} | T:1-I |  |  | Slot 6 Ch 1 |  | IDA_OP2_Mir1B_Msk_T1 | Drop_1:6:I.Ch1Data | Local:2:I.Data.14 | IDA_T_I[10] | 1
270 | XF:23IDA-OP:2{Mir:1A} | T:1-I |  |  | Slot 3 Ch 1 |  | IDA_OP2_Mir1A_T1 | Drop_1:3:I.Ch1Data | Local:2:I.Data.15 | IDA_T_I[11] | 1
271 | XF:23IDA-OP:2{Mir:1B} | T:1-I |  |  | Slot 5 Ch 1 |  | IDA_OP2_Mir1B_T1 | Drop_1:5:I.Ch1Data |  | IDA_T_I[12] | 1
272 | XF:23IDA-OP:2{Mir:1A-Msk} | T:2-I |  |  | Slot 5 Ch 0 |  | IDA_OP2_Mir1A_Msk_T2 | Drop_1:5:I.Ch0Data |  | IDA_T_I[13] | 1
273 | XF:23IDA-OP:2{Mir:1B-Msk} | T:2-I |  |  | Slot 7 Ch 0 |  | IDA_OP2_Mir1B_Msk_T2 | Drop_1:7:I.Ch0Data | Local:2:I.Data.16 | IDA_T_I[14] | 1
274 | XF:23IDA-OP:2{Mir:1A} | T:2-I |  |  | Slot 4 Ch 0 |  | IDA_OP2_Mir1A_T2 | Drop_1:4:I.Ch0Data |  | IDA_T_I[15] | 1
275 | XF:23IDA-OP:2{Mir:1B} | T:2-I |  |  | Slot 6 Ch 0 |  | IDA_OP2_Mir1B_T2 | Drop_1:6:I.Ch0Data |  | IDA_T_I[16] | 1
276 | XF:23IDA-OP:2{Msk:1} | T:1-I |  |  | Slot 12 Ch 0 |  | IDA_OP2_Msk1_T1 | Drop_1:12:I.Ch0Data |  | IDA_T_I[17] | 1
277 | XF:23IDA-OP:2{Msk:1} | T:2-I |  |  | Slot 12 Ch 1 |  | IDA_OP2_Msk1_T2 | Drop_1:12:I.Ch1Data | Local:3:O.Data.5 | IDA_T_I[18] | 1
278 | XF:23IDA-VA:0{DP:1} | T-I |  |  | Slot 7 Ch 1 |  | IDA_VA0_DP1_T | Drop_1:7:I.Ch1Data | Local:2:I.Data.17 | IDA_T_I[19] | 1
256 | XF:23IDA-UT{DI} | T:Supply-I | DI RTD Supply |  | Slot 13 Ch 0 |  | IDA_UT_DI_T_Spply | Drop_1:13:I.Ch0Data |  | IDA_T_I[20] | 1
257 | XF:23IDA-UT{DI} | T:Return-I | DI RTD Return |  | Slot 13 Ch 1 |  | IDA_UT_DI_T_Rtrn | Drop_1:13:I.Ch1Data |  | IDA_T_I[21] | 1
259 | XF:23IDA-UT{PCW} | T:Supply-I |  |  | Slot 14 Ch 0 |  | IDA_UT_PCW_T_Spply | Drop_1:14:I.Ch0Data |  | IDA_T_I[22] | 1
260 | XF:23IDA-UT{PCW} | T:Return-I |  |  | Slot 14 Ch 1 |  | IDA_UT_PCW_T_Rtrn | Drop_1:14:I.Ch1Data |  | IDA_T_I[23] | 1
279 | XF:23ID1-OP{Diag:02} | T-I |  |  |  |  | ID1_OP_Diag02_T | Armor_03:I.Ch0Data | Local:2:I.Data.18 | ID1_T_I[0] | 1
280 | XF:23ID1-OP{Mon-Mir} | T-I |  |  |  |  | ID1_OP_Mon_Mir_T | Drop_3:9:I.Ch0Data |  | ID1_T_I[1] | 1
281 | XF:23ID1-OP{Mon-Mir:Msk} | T-I |  |  |  |  | ID1_OP_Mon_MirMsk_T | Drop_3:9:I.Ch1Data |  | ID1_T_I[2] | 1
282 | XF:23ID1-OP{Mon-Grt:1} | T-I |  |  |  |  | ID1_OP_Mon_Grt1_T | Drop_3:7:I.Ch0Data | Local:2:I.Data.19 | ID1_T_I[3] | 1
283 | XF:23ID1-OP{Mon-Grt:2} | T-I |  |  |  |  | ID1_OP_Mon_Grt2_T | Drop_3:7:I.Ch1Data | Local:2:I.Data.20 | ID1_T_I[4] | 1
284 | XF:23ID1-OP{Mon-Grt:3} | T-I |  |  |  |  | ID1_OP_Mon_Grt3_T | Drop_3:8:I.Ch0Data |  | ID1_T_I[5] | 1
285 | XF:23ID1-OP{Mon-Grt:4} | T-I |  |  |  |  | ID1_OP_Mon_Grt4_T | Drop_3:8:I.Ch1Data | Local:2:I.Data.21 | ID1_T_I[6] | 1
286 | XF:23ID1-OP{Mir:3-Bdr} | T-I |  |  |  |  | ID1_OP_Mir3_Bdr_T | Armor_05:I.Ch0Data |  | ID1_T_I[7] | 1
287 | XF:23ID2-OP{Diag:01} | T-I |  |  |  |  | ID2_OP_Diag01_T | Armor_14:I.Ch0Data |  | ID2_T_I[0] | 1
288 | XF:23ID2-OP{Mon-Mir} | T-I |  |  |  |  | ID2_OP_Mon_Mir_T | Drop_4:9:I.Ch0Data |  | ID2_T_I[1] | 1
289 | XF:23ID2-OP{Mon-Mir:Msk} | T-I |  |  |  |  | ID2_OP_Mon_MirMsk_T | Drop_4:9:I.Ch1Data |  | ID2_T_I[2] | 1
290 | XF:23ID2-OP{Mon-Grt:1} | T-I |  |  |  |  | ID2_OP_Mon_Grt1_T | Drop_4:7:I.Ch0Data |  | ID2_T_I[3] | 1
291 | XF:23ID2-OP{Mon-Grt:2} | T-I |  |  |  |  | ID2_OP_Mon_Grt2_T | Drop_4:7:I.Ch1Data |  | ID2_T_I[4] | 1
292 | XF:23ID2-OP{Mon-Grt:3} | T-I |  |  |  |  | ID2_OP_Mon_Grt3_T | Drop_4:8:I.Ch0Data |  | ID2_T_I[5] | 1
293 | XF:23ID2-OP{Mon-Grt:4} | T-I |  |  |  |  | ID2_OP_Mon_Grt4_T | Drop_4:8:I.Ch1Data |  | ID2_T_I[6] | 1
294 | XF:23ID2-OP{Chop} | T-I |  |  |  |  | ID2_OP_Chop_T | Armor_20:I.Ch0Data |  | ID2_T_I[7] | 1
295 | XF:23IDA-VA:0{DP:1} | F-I | DP Head 2 |  |  |  | IDA_VA0_DP1_F | Drop_2:13:I.Ch1Data |  | F_I[0] | F_Sts[0] | 0.0014 | GPM | 0.425 | 303 | 0.25 | 178
296 | XF:23IDA-OP:1{Mir:1} | F-I | DP Head 3 |  |  |  | IDA_OP1_Mir1_F | Drop_2:13:I.Ch2Data |  | F_I[1] | F_Sts[1] | 0.0023 | GPM | 1.275 | 554 | 0.75 | 326
297 | XF:23IDA-OP:1{Mir:1-Msk} | F-I | DP Head 4 |  |  |  | IDA_OP1_Mir1_Msk_F | Drop_2:13:I.Ch3Data |  | F_I[2] | F_Sts[2] | 0.0023 | GPM | 1.275 | 554 | 0.75 | 326
298 | XF:23IDA-OP:2{Mir:1A} | F-I | DP Head 8 |  |  |  | IDA_OP2_Mir1A_F | Drop_2:13:I.Ch6Data |  | F_I[3] | F_Sts[3] | 0.0023 | GPM | 0.68 | 295 | 0.4 | 173
299 | XF:23IDA-OP:2{Mir:1-Msk} | F-I | DP Head 7 |  |  |  | IDA_OP2_Mir1_Msk_F | Drop_2:13:I.Ch5Data |  | F_I[4] | F_Sts[4] | 0.0014 | GPM | 0.68 | 485 | 0.4 | 285
300 | XF:23IDA-OP:1{FS:1} | F-I | DP Head 6 |  |  |  | IDA_OP1_FS1_F | Drop_2:13:I.Ch4Data |  | F_I[5] | F_Sts[5] | 0.00055 | GPM | 0.425 | 772 | 0.25 | 454
301 | XF:23IDA-OP:2{Mir:1B} | F-I | DP Head 9 |  |  |  | IDA_OP2_Mir1B_F | Drop_2:13:I.Ch7Data |  | F_I[6] | F_Sts[6] | 0.0023 | GPM | 0.68 | 295 | 0.4 | 173
302 | XF:23ID1-OP{Mon-Mir} | F-I | DP Head 19 |  |  |  | ID1_OP_Mon_Mir_F | Drop_2:15:I.Ch1Data |  | F_I[7] | F_Sts[7] | 0.0014 | GPM | 0.765 | 546 | 0.45 | 321
303 | XF:23ID1-OP{Mon-Grt} | F-I | DP Head 20 |  |  |  | ID1_OP_Mon_Grt_F | Drop_2:15:I.Ch2Data |  | F_I[8] | F_Sts[8] | 0.0014 | GPM | 0.425 | 303 | 0.25 | 178
304 | XF:23ID1-OP{Diag:02} | F-I | DP Head 21 |  |  |  | ID1_OP_Diag02_F | Drop_2:15:I.Ch3Data |  | F_I[9] | F_Sts[9] | 0.00055 | GPM | 0.255 | 463 | 0.15 | 272
305 | XF:23ID2-OP{Mon-Mir} | F-I | DP Head 15 |  |  |  | ID2_OP_Mon_Mir_F | Drop_2:14:I.Ch6Data |  | F_I[10] | F_Sts[10] | 0.0014 | GPM | 0.765 | 546 | 0.45 | 321
306 | XF:23ID2-OP{Mon-Grt} | F-I | DP Head 16 |  |  |  | ID2_OP_Mon_Grt_F | Drop_2:14:I.Ch7Data |  | F_I[11] | F_Sts[11] | 0.0014 | GPM | 0.425 | 303 | 0.25 | 178
307 | XF:23ID2-OP{Diag:01} | F-I | DP Head 17 |  |  |  | ID2_OP_Diag01_F | Drop_2:15:I.Ch0Data |  | F_I[12] | F_Sts[12] | 0.00055 | GPM | 0.255 | 463 | 0.15 | 272
308 | XF:23IDA-OP:0{Msk:1} | F-I | DP Head 5 |  |  |  | IDA_OP0_Msk1_F | Drop_2:15:I.Ch6Data |  | F_I[13] | F_Sts[13] | 0.0032 | GPM | 2.7 | 843
309 | XF:23IDA-OP:1{Msk:1} | F-I | DP Head 5 |  |  |  | IDA_OP1_Msk1_F | Drop_2:16:I.Ch3Data |  | F_I[14] | F_Sts[14] | 0.0032 | GPM | 0.7 | 218
310 | XF:23IDA-OP:2{Msk:1} | F-I | DP Head 11 |  |  |  | IDA_OP2_Msk1_F | Drop_2:16:I.Ch4Data |  | F_I[15] | F_Sts[15] | 0.0032 | GPM | 0.7 | 218
311 | XF:23IDA-OP:1{PSh} | F-I | DP Head 13 |  |  |  | IDA_OP1_PSh_F | Drop_2:16:I.Ch0Data |  | F_I[16] | F_Sts[16] | 0.001 | GPM | 0.45 | 450
312 | XF:23IDA-OP:2{PSh} | F-I | DP Head 13 |  |  |  | IDA_OP2_PSh_F | Drop_2:16:I.Ch5Data |  | F_I[17] | F_Sts[17] | 0.001 | GPM | 0.45 | 450
313 | XF:23ID1-OP{Mon-Msk} | F-I | DP Head 18 |  |  |  | ID1_OP_Mon_Msk_F | Drop_2:16:I.Ch7Data |  | F_I[18] | F_Sts[18] | 0.0019 | GPM
314 | XF:23ID2-OP{Mon-Msk} | F-I | DP Head 14 |  |  |  | ID2_OP_Mon_Msk_F | Drop_2:16:I.Ch6Data |  | F_I[19] | F_Sts[19] | 0.0019 | GPM
315 | XF:23IDA-UT{Circuit:1} | F-I | 1 |  |  |  | IDA_UT_Circuit1_F | Drop_2:13:I.Ch0Data |  | F_I[20] | F_Sts[20] | 0.00055 | GPM
316 | XF:23IDA-UT{Circuit:10} | F-I | 10 |  |  |  | IDA_UT_Circuit10_F | Drop_2:14:I.Ch0Data |  | F_I[21] | F_Sts[21] | 0.0023 | GPM
317 | XF:23IDA-UT{DI} | F-I | Master |  |  |  | IDA_UT_DI_F | Drop_2:14:I.Ch2Data |  | F_I[22] | F_Sts[22] | 0.02 | GPM
318 | XF:23IDA-UT{DI} | P:Supply-I | DI Pressure Supply |  |  |  | IDA_UT_DI_P_Spply | Drop_2:14:I.Ch3Data |  | P_Spply | F_Sts[23] | 0.15 | PSIG
319 | XF:23IDA-UT{DI} | P:Return-I | DI Pressure Return |  |  |  | IDA_UT_DI_P_Rtrn | Drop_2:14:I.Ch4Data |  | P_Rtrn | F_Sts[24] | 0.15 | PSIG
320 | XF:23ID1-UT{DI} | P:Supply-I | DI Pressure Supply On Floor |  |  |  | ID1_UT_DI_P_Spply | Drop_2:15:I.Ch4Data |  | F_I[25] | F_Sts[25] | 0.15 | PSIG
321 | XF:23ID1-UT{DI} | P:Return-I | DI Pressure Return On Floor |  |  |  | ID1_UT_DI_P_Rtrn | Drop_2:15:I.Ch5Data |  | F_I[26] | F_Sts[26] | 0.15 | PSIG
322 | XF:23IDA-UT{DI-Vlv:Supply} | Act-Sts | DI Supply valve in FOE energized? |  |  |  | IDA_UT_DISupplyVlvAct_Sts | Drop_2:O.Data[9].2 |  | FOE_Sply_Sts.Coil1 | IDA_UT_DISupplyVlvAct_Sts | IDA_UT_DISupplyVlvAct_Sts
323 | XF:23IDA-UT{DI-Vlv:Supply} | ClsLim-Sts | DI Supply valve in FOE Closed limit sts |  |  |  | IDA_UT_DISupplyVlvClsLim_Sts | Drop_2:I.Data[5].2 |  | FOE_Sply_Sts.ClsSw | IDA_UT_DISupplyVlvClsLim_Sts | IDA_UT_DISupplyVlvClsLim_Sts
324 | XF:23IDA-UT{DI-Vlv:Supply} | OpnLim-Sts | DI Supply valve in FOE Open limit sts |  |  |  | IDA_UT_DISupplyVlvOpnLim_Sts | Drop_2:I.Data[5].1 |  | FOE_Sply_Sts.OpnSw | IDA_UT_DISupplyVlvOpnLim_Sts | IDA_UT_DISupplyVlvOpnLim_Sts
325 | XF:23IDA-UT{DI-Vlv:Return} | Act-Sts | DI Return valve in FOE valve energized? |  |  |  | IDA_UT_DIReturnVlvAct_Sts | Drop_2:O.Data[10].1 |  | FOE_Rtrn_Sts.Coil1 | IDA_UT_DIReturnVlvAct_Sts | IDA_UT_DIReturnVlvAct_Sts
326 | XF:23IDA-UT{DI-Vlv:Return} | ClsLim-Sts | DI Return valve in FOE valve Closed limit sts |  |  |  | IDA_UT_DIReturnVlvClsLim_Sts | Drop_2:I.Data[5].4 |  | FOE_Rtrn_Sts.ClsSw | IDA_UT_DIReturnVlvClsLim_Sts | IDA_UT_DIReturnVlvClsLim_Sts
327 | XF:23IDA-UT{DI-Vlv:Return} | OpnLim-Sts | DI Return valve in FOE valve Open limit sts |  |  |  | IDA_UT_DIReturnVlvOpnLim_Sts | Drop_2:I.Data[5].3 |  | FOE_Rtrn_Sts.OpnSw | IDA_UT_DIReturnVlvOpnLim_Sts | IDA_UT_DIReturnVlvOpnLim_Sts
328 | XF:23ID-UT{PCW-Vlv:Supply} | Act-Sts | DI Supply valve on Floor energized? |  |  |  | ID_UT_DISupplyVlvAct_Sts | Drop_2:O.Data[10].2 |  | Floor_Sply_Sts.Coil1 | ID_UT_DISupplyVlvAct_Sts | ID_UT_DISupplyVlvAct_Sts
329 | XF:23ID-UT{PCW-Vlv:Supply} | ClsLim-Sts | DI Supply valve on Floor Closed limit sts |  |  |  | ID_UT_DISupplyVlvClsLim_Sts | Drop_2:I.Data[5].6 |  | Floor_Sply_Sts.ClsSw | ID_UT_DISupplyVlvClsLim_Sts | ID_UT_DISupplyVlvClsLim_Sts
330 | XF:23ID-UT{PCW-Vlv:Supply} | OpnLim-Sts | DI Supply valve on Floor Open limit sts |  |  |  | ID_UT_DISupplyVlvOpnLim_Sts | Drop_2:I.Data[5].5 |  | Floor_Sply_Sts.OpnSw | ID_UT_DISupplyVlvOpnLim_Sts | ID_UT_DISupplyVlvOpnLim_Sts
331 | XF:23ID-UT{PCW-Vlv:Return} | Act-Sts | DI Return valve on Floor valve energized? |  |  |  | ID_UT_DIReturnVlvAct_Sts | Drop_2:O.Data[10].7 |  | Floor_Rtrn_Sts.Coil1 | ID_UT_DIReturnVlvAct_Sts | ID_UT_DIReturnVlvAct_Sts
332 | XF:23ID-UT{PCW-Vlv:Return} | ClsLim-Sts | DI Return valve on Floor valve Closed limit sts |  |  |  | ID_UT_DIReturnVlvClsLim_Sts | Drop_2:I.Data[6].0 |  | Floor_Rtrn_Sts.ClsSw | ID_UT_DIReturnVlvClsLim_Sts | ID_UT_DIReturnVlvClsLim_Sts
333 | XF:23ID-UT{PCW-Vlv:Return} | OpnLim-Sts | DI Return valve on Floor valve Open limit sts |  |  |  | ID_UT_DIReturnVlvOpnLim_Sts | Drop_2:I.Data[5].7 |  | Floor_Rtrn_Sts.OpnSw | ID_UT_DIReturnVlvOpnLim_Sts | ID_UT_DIReturnVlvOpnLim_Sts
334 | XF:23ID{RG:A-Det:Smk} | Alrm-Sts | Smoke |  |  |  | ID_RGA_DetSmkAlrm_Sts | Drop_2:I.Data[6].2 |  | Smoke_Sts[0]
335 | XF:23ID{RG:A-Det:Smk} | Sts:Head-Sts | Missing head |  |  |  | ID_RGA_DetSmkStsHead_Sts | Drop_2:I.Data[6].3 |  | Smoke_Sts[1]
336 | XF:23ID{RG:B-Det:Smk} | Alrm-Sts | Smoke |  |  |  | ID_RGB_DetSmkAlrm_Sts | Drop_2:I.Data[6].4 |  | Smoke_Sts[2]
337 | XF:23ID{RG:B-Det:Smk} | Sts:Head-Sts | Missing head |  |  |  | ID_RGB_DetSmkStsHead_Sts | Drop_2:I.Data[6].5 |  | Smoke_Sts[3]
338 | XF:23ID{RG:C-Det:Smk} | Alrm-Sts | Smoke |  |  |  | ID_RGC_DetSmkAlrm_Sts | Drop_2:I.Data[6].6 |  | Smoke_Sts[4]
339 | XF:23ID{RG:C-Det:Smk} | Sts:Head-Sts | Missing head |  |  |  | ID_RGC_DetSmkStsHead_Sts | Drop_2:I.Data[6].7 |  | Smoke_Sts[5]
340 | XF:23ID{RG:D-Det:Smk} | Alrm-Sts | Smoke |  |  |  | ID_RGD_DetSmkAlrm_Sts | Drop_2:I.Data[8].0 |  | Smoke_Sts[6]
341 | XF:23ID{RG:D-Det:Smk} | Sts:Head-Sts | Missing head |  |  |  | ID_RGD_DetSmkStsHead_Sts | Drop_2:I.Data[8].1 |  | Smoke_Sts[7]
342 | XF:23ID{RG:E-Det:Smk} | Alrm-Sts | Smoke |  |  |  | ID_RGE_DetSmkAlrm_Sts | Drop_2:I.Data[8].2 |  | Smoke_Sts[8]
343 | XF:23ID{RG:E-Det:Smk} | Sts:Head-Sts | Missing head |  |  |  | ID_RGE_DetSmkStsHead_Sts | Drop_2:I.Data[8].3 |  | Smoke_Sts[9]
344 | XF:23ID{RG:F-Det:Smk} | Alrm-Sts | Smoke |  |  |  | ID_RGF_DetSmkAlrm_Sts | Drop_2:I.Data[8].4 |  | Smoke_Sts[10]
345 | XF:23ID{RG:F-Det:Smk} | Sts:Head-Sts | Missing head |  |  |  | ID_RGF_DetSmkStsHead_Sts | Drop_2:I.Data[8].5 |  | Smoke_Sts[11]
346 | XF:23IDA-PU{LD:1} | Alrm-Sts | Hutch A FOE floor Leak detector |  |  |  | IDA_PU_LD1Alrm_Sts | Drop_2:I.Data[5].0 |  | Misc_Sts[4]
347 | XF:23IDA-BI:1[FS:1} | Sts:Out-Sts |  |  |  |  | IDA_BI1_FS1Out_Sts | Drop_2:I.Data[2].4 |  | Misc_Sts[5]
348 | XF:23IDA-BI:1[FS:1} | Sts:Pk-Sts |  |  |  |  | IDA_BI1_FS1Pk_Sts | Drop_2:I.Data[2].5 |  | Misc_Sts[6]
349 | XF:23IDA-BI:1[FS:1} | Sts:Wh-Sts |  |  |  |  | IDA_BI1_FS1Wh_Sts | Drop_2:I.Data[2].6 |  | Misc_Sts[7]

## EPICS db Aliases
record( | bi | , " | XF:23IDA-VA:0{Diag:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[0] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Msk:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[1] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[2] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[3] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[4] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[5] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{PSh-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[6] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{PSh-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[7] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[8] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[9] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[10] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[11] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[12] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:2-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[13] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[14] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[15] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[16] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[17] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[18] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[19] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[20] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[21] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[22] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{PSh-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[23] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[24] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[25] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[26] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[27] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[28] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[29] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[30] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_1[31] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-IP:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Sts_2[0] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Diag:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[0] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Msk:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[1] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[2] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[3] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[4] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{PSh-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[5] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{PSh-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[6] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[7] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[8] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[9] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[10] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[11] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:2-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[12] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[13] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[14] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[15] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[16] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[17] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[18] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[19] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[20] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[21] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{PSh-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[22] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[23] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[24] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[25] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[26] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[27] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[28] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[29] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[30] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_1[31] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-CCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Sts_2[0] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Diag:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[0] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Msk:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[1] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[2] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[3] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[4] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{PSh-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[5] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{PSh-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[6] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[7] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[8] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[9] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[10] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[11] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:2-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[12] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[13] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[14] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[15] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[16] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[17] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[18] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[19] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[20] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[21] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{PSh-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[22] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[23] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[24] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[25] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[26] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[27] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[28] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[29] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[30] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_1[31] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-TCG:1}Sts:Rly1PLC-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | TCG_Sts_2[0] | ")NL | field( | ZNAM | , " | Relay Open | ")NL | field( | ONAM | , " | Relay Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_01_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_02_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Sw:OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_01_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_02_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Sw:ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Sts:Coil-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-Vlv}Rdy-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[0] | ")NL | field( | ZNAM | , " | Not Ready | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-Vlv}Intlk:Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[1] | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-Vlv}Intlk:Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[2] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-Vlv}Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[3] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-Vlv}Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[4] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-GV}Intlk:Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[5] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-GV}Intlk:Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[6] | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-GV}Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-GV}Rdy-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[8] | ")NL | field( | ZNAM | , " | Not Ready | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-GV}Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[9] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-GV}Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[10] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV-GV}Cmd:Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[11] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-Vlv}Cmd:Rdy-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[12] | ")NL | field( | ZNAM | , " | Not Ready | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-Vlv}Intlk:Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[13] | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-Vlv}Intlk:Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[14] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-Vlv}Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[15] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-Vlv}Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[16] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-GV}Intlk:Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[17] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-GV}Intlk:Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[18] | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-GV}Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[19] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-GV}Rdy-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[20] | ")NL | field( | ZNAM | , " | Not Ready | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-GV}Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[21] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-GV}Cmd:Opn-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[22] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV-GV}Cmd:Cls-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_Sts[23] | [40 empty] | ")NL}NL
record( | bi | , " | XF:23ID-EPS{}Out:EPS_Permit-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Misc_Sts[6] | ")NL | field( | ZNAM | , " | User Interlock | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | #REF! | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH_FE_Sts.EnableRaw | ")NL | field( | ZNAM | , " | Not secured | ")NL | field( | ONAM | , " | Ready | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Enbl-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH_FE_Sts.StatusRaw | ")NL | field( | ZNAM | , " | Fault | ")NL | field( | ONAM | , " | Able to open | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Cmd:Open-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH_FE_Sts.CMDRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Open | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Cmd:Close-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH_FE_Sts.OpenRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Close | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Sts:Pos-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH_FE_Sts.CloseRaw | ")NL | field( | ZNAM | , " | Open | ")NL | field( | ONAM | , " | Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Sts:OpnCmd-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_1_Sts.EnableRaw | ")NL | field( | ZNAM | , " | Cleared | ")NL | field( | ONAM | , " | Latched | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Sts:OpnCmd-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_1_Sts.CMDRaw | ")NL | field( | ZNAM | , " | Fault | ")NL | field( | ONAM | , " | Able to open | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Cmd:Open-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_1_Sts.OpenRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Open | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Cmd:Close-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_1_Sts.CloseRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Close | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Enbl-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_2_Sts.EnableRaw | ")NL | field( | ZNAM | , " | Open | ")NL | field( | ONAM | , " | Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Sts:Pos-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_2_Sts.StatusRaw | ")NL | field( | ZNAM | , " | Fault | ")NL | field( | ONAM | , " | Able to open | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Cmd:Open-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_2_Sts.CMDRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Open | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Cmd:Close-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_2_Sts.OpenRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Close | [30 empty] | ")NL}NL
record( | bi | , " | #REF! | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_2_Sts.CloseRaw | ")NL | field( | ZNAM | , " | Open | ")NL | field( | ONAM | , " | Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Enbl-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_3_Sts.EnableRaw | ")NL | field( | ZNAM | , " | Fault | ")NL | field( | ONAM | , " | Able to open | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Sts:Pos-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_3_Sts.StatusRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Open | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Sts:OpnCmd-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_3_Sts.CMDRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Close | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Cmd:Open-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_3_Sts.OpenRaw | ")NL | field( | ZNAM | , " | Open | ")NL | field( | ONAM | , " | Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Enbl-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_4_Sts.EnableRaw | ")NL | field( | ZNAM | , " | Fault | ")NL | field( | ONAM | , " | Able to open | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Sts:Pos-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_4_Sts.StatusRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Open | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Sts:OpnCmd-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_4_Sts.CMDRaw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Close | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Cmd:Open-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PSH_4_Sts.OpenRaw | ")NL | field( | ZNAM | , " | Open | ")NL | field( | ONAM | , " | Closed | ")NL | field( | ZSV | , " | MINOR | [25 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-OP:0{Msk:1}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[0] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:0{Msk:1}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[1] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Mir:1-Msk}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[2] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Mir:1-Msk}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[3] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Mir:1}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[4] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Mir:1}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[5] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Msk:1}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[6] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Msk:1}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[7] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{FS:1}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[8] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1A-Msk}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[9] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1B-Msk}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[10] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1A}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[11] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1B}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[12] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1A-Msk}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[13] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1B-Msk}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[14] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1A}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[15] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1B}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[16] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Msk:1}T:1-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[17] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Msk:1}T:2-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[18] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-VA:0{DP:1}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[19] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-UT{DI}T:Supply-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[20] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-UT{DI}T:Return-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[21] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-UT{PCW}T:Supply-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[22] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-UT{PCW}T:Return-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_I[23] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Diag:02}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[0] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Mir}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[1] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Mir:Msk}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[2] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Grt:1}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[3] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Grt:2}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[4] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Grt:3}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[5] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Grt:4}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[6] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mir:3-Bdr}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_I[7] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Diag:01}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[0] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Mir}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[1] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Mir:Msk}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[2] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Grt:1}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[3] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Grt:2}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[4] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Grt:3}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[5] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Grt:4}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[6] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Chop}T-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_I[7] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.1 | ")NL | field( | PREC | , " | 1 | ")NL | field( | EGU | , " | C | ")NL | field( | HIGH | , " | 40 | ")NL | field( | HSV | , " | MINOR | ")NL | field( | HIHI | , " | 75 | ")NL | field( | HHSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-VA:0{DP:1}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[0] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0014 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.425 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.25 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Mir:1}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[1] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0023 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 1.275 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.75 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Mir:1-Msk}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[2] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0023 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 1.275 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.75 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1A}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[3] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0023 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.68 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.4 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1-Msk}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[4] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0014 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.68 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.4 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{FS:1}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[5] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.00055 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.425 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.25 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Mir:1B}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[6] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0023 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.68 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.4 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Mir}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[7] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0014 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.765 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.45 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Grt}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[8] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0014 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.425 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.25 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Diag:02}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[9] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.00055 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.255 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.15 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Mir}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[10] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0014 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.765 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.45 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Grt}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[11] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0014 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.425 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.25 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Diag:01}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[12] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.00055 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.255 | ")NL | field( | LSV | , " | MINOR | ")NL | field( | LOLO | , " | 0.15 | ")NL | field( | LLSV | , " | MAJOR | ")NL}NL
record( | ai | , " | XF:23IDA-OP:0{Msk:1}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[13] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0032 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 2.7 | ")NL | field( | LSV | , " | MINOR | [10 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{Msk:1}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[14] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0032 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.7 | ")NL | field( | LSV | , " | MINOR | [10 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{Msk:1}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[15] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0032 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.7 | ")NL | field( | LSV | , " | MINOR | [10 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-OP:1{PSh}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[16] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.001 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.45 | ")NL | field( | LSV | , " | MINOR | [10 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-OP:2{PSh}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[17] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.001 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | ")NL | field( | LOW | , " | 0.45 | ")NL | field( | LSV | , " | MINOR | [10 empty] | ")NL}NL
record( | ai | , " | XF:23ID1-OP{Mon-Msk}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[18] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0019 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | [20 empty] | ")NL}NL
record( | ai | , " | XF:23ID2-OP{Mon-Msk}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[19] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0019 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | [20 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-UT{Circuit:1}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[20] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.00055 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | [20 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-UT{Circuit:10}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[21] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.0023 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | [20 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-UT{DI}F-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[22] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.02 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | GPM | [20 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-UT{DI}P:Supply-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | P_Spply | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.15 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | PSIG | [20 empty] | ")NL}NL
record( | ai | , " | XF:23IDA-UT{DI}P:Return-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | P_Rtrn | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.15 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | PSIG | [20 empty] | ")NL}NL
record( | ai | , " | XF:23ID1-UT{DI}P:Supply-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[25] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.15 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | PSIG | [20 empty] | ")NL}NL
record( | ai | , " | XF:23ID1-UT{DI}P:Return-I | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_I[26] | ")NL | field( | LINR | , " | SLOPE | ")NL | field( | ESLO | , " | 0.15 | ")NL | field( | PREC | , " | 2 | ")NL | field( | EGU | , " | PSIG | [20 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Supply}Act-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Supply}ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Supply}OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Return}Act-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Return}ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Return}OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Supply}Act-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Supply}ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Supply}OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Return}Act-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Sts.Coil1 | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | Energized | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Return}ClsLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Sts.ClsSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Return}OpnLim-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Sts.OpnSw | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | In Position | [30 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:A-Det:Smk}Alrm-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[0] | ")NL | field( | ZNAM | , " | OK | ")NL | field( | ONAM | , " | Smoke | [5 empty] | ")NL | field( | OSV | , " | MAJOR | [20 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:A-Det:Smk}Sts:Head-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[1] | ")NL | field( | ZNAM | , " | Missing Head | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:B-Det:Smk}Alrm-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[2] | ")NL | field( | ZNAM | , " | OK | ")NL | field( | ONAM | , " | Smoke | [5 empty] | ")NL | field( | OSV | , " | MAJOR | [20 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:B-Det:Smk}Sts:Head-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[3] | ")NL | field( | ZNAM | , " | Missing Head | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:C-Det:Smk}Alrm-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[4] | ")NL | field( | ZNAM | , " | OK | ")NL | field( | ONAM | , " | Smoke | [5 empty] | ")NL | field( | OSV | , " | MAJOR | [20 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:C-Det:Smk}Sts:Head-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[5] | ")NL | field( | ZNAM | , " | Missing Head | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:D-Det:Smk}Alrm-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[6] | ")NL | field( | ZNAM | , " | OK | ")NL | field( | ONAM | , " | Smoke | [5 empty] | ")NL | field( | OSV | , " | MAJOR | [20 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:D-Det:Smk}Sts:Head-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[7] | ")NL | field( | ZNAM | , " | Missing Head | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:E-Det:Smk}Alrm-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[8] | ")NL | field( | ZNAM | , " | OK | ")NL | field( | ONAM | , " | Smoke | [5 empty] | ")NL | field( | OSV | , " | MAJOR | [20 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:E-Det:Smk}Sts:Head-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[9] | ")NL | field( | ZNAM | , " | Missing Head | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:F-Det:Smk}Alrm-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[10] | ")NL | field( | ZNAM | , " | OK | ")NL | field( | ONAM | , " | Smoke | [5 empty] | ")NL | field( | OSV | , " | MAJOR | [20 empty] | ")NL}NL
record( | bi | , " | XF:23ID{RG:F-Det:Smk}Sts:Head-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Smoke_Sts[11] | ")NL | field( | ZNAM | , " | Missing Head | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | [25 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-PU{LD:1}Alrm-Sts | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Misc_Sts[4] | ")NL | field( | ZNAM | , " | Leak | ")NL | field( | ONAM | , " | OK | [5 empty] | ")NL | field( | ZSV | , " | MAJOR | [20 empty] | ")NL}NL

## EPICS db Latch
record( | bi | , " | XF:23IDA-VA:0{Diag:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Msk:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[1] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[2] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[3] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[4] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[5] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{PSh-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[6] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{PSh-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[8] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[9] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[10] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[11] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[12] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:2-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[13] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[14] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[15] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[16] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[17] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[18] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[19] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[20] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[21] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[22] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{PSh-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[23] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[24] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[25] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[26] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[27] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[28] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[29] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[30] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_1[31] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-IP:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IP_Lock_2[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Diag:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{Msk:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[1] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[2] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[3] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[4] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{PSh-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[5] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{PSh-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[6] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[8] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[9] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[10] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[11] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:2-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[12] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[13] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[14] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[15] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[16] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[17] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[18] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[19] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[20] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[21] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{PSh-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[22] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[23] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[24] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[25] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[26] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[27] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[28] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[29] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[30] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_1[31] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-CCG:1}Sts:Rly1PLC-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | CCG_Lock_2[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[1] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[2] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[3] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[4] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[5] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[6] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[8] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[9] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[10] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[11] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[12] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[13] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[14] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[15] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[16] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[17] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[18] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[19] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[20] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[21] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[22] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[23] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[24] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[25] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[26] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[27] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[28] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[29] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[30] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Pos-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_OpnSw_Lock[31] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:0{Msk:1}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:0{Msk:1}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[1] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1-Msk}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[2] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1-Msk}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[3] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[4] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[5] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Msk:1}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[6] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Msk:1}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{FS:1}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[8] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A-Msk}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[9] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B-Msk}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[10] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[11] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[12] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A-Msk}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[13] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B-Msk}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[14] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[15] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[16] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Msk:1}T:1-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[17] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Msk:1}T:2-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[18] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[19] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}T:Supply-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[20] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}T:Return-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[21] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{PCW}T:Supply-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[22] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{PCW}T:Return-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Lock[23] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Diag:02}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Mir}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[1] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Mir:Msk}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[2] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:1}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[3] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:2}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[4] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:3}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[5] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:4}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[6] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mir:3-Bdr}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Lock[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Diag:01}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Mir}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[1] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Mir:Msk}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[2] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:1}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[3] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:2}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[4] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:3}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[5] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:4}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[6] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Chop}T-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Lock[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[0] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[1] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1-Msk}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[2] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[3] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1-Msk}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[4] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{FS:1}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[5] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[6] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Mir}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[7] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[8] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Diag:02}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[9] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Mir}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[10] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[11] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Diag:01}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[12] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:0{Msk:1}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[13] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Msk:1}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[14] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Msk:1}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[15] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{PSh}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[16] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{PSh}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[17] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Msk}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[18] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Msk}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[19] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{Circuit:1}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[20] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{Circuit:10}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[21] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}F-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[22] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}P:Supply-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[23] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}P:Return-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[24] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-UT{DI}P:Supply-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[25] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-UT{DI}P:Return-First | ")NL{NL | field( | SCAN | , " | 1 | second | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Lock[26] | ")NL | field( | ZNAM | , " | None | ")NL | field( | ONAM | , " | First | ")NL | field( | OSV | , " | MAJOR | ")NL}NL

## PLC EPS Base
Index | Component | Signal | PLC Tag Name (optional) | TAG or ALIAS | ATTRIBUTES | Temp:emulation | Array element in Global tag | DINT used
1 | XF:23IDA-VA:0{DP:1-GV:1} | Pos-Sts |  |  |  |  | GV_01_Sts.Sts
2 | XF:23IDA-VA:0{DP:1-GV:1} | Err-Sts |  |  |  |  | GV_01_Sts.StsFault
3 | XF:23IDA-VA:0{DP:1-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_01_Sts.FailedToOpn
4 | XF:23IDA-VA:0{DP:1-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_01_Sts.FailedToCls
5 | XF:23IDA-VA:0{DP:1-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_01_Sts.LockUS
6 | XF:23IDA-VA:0{DP:1-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_01_Sts.LockDS
7 | XF:23IDA-VA:0{DP:1-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_01_Cmd.OpnCmd
8 | XF:23IDA-VA:0{DP:1-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_01_Cmd.ClsCmd
9 | XF:23IDA-VA:1{Mir:1-GV:1} | Pos-Sts |  |  |  |  | GV_02_Sts.Sts
10 | XF:23IDA-VA:1{Mir:1-GV:1} | Err-Sts |  |  |  |  | GV_02_Sts.StsFault
11 | XF:23IDA-VA:1{Mir:1-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_02_Sts.FailedToOpn
12 | XF:23IDA-VA:1{Mir:1-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_02_Sts.FailedToCls
13 | XF:23IDA-VA:1{Mir:1-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_02_Sts.LockUS
14 | XF:23IDA-VA:1{Mir:1-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_02_Sts.LockDS
15 | XF:23IDA-VA:1{Mir:1-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_02_Cmd.OpnCmd
16 | XF:23IDA-VA:1{Mir:1-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_02_Cmd.ClsCmd
17 | XF:23IDA-VA:1{FS:1-GV:1} | Pos-Sts |  |  |  |  | GV_03_Sts.Sts
18 | XF:23IDA-VA:1{FS:1-GV:1} | Err-Sts |  |  |  |  | GV_03_Sts.StsFault
19 | XF:23IDA-VA:1{FS:1-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_03_Sts.FailedToOpn
20 | XF:23IDA-VA:1{FS:1-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_03_Sts.FailedToCls
21 | XF:23IDA-VA:1{FS:1-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_03_Sts.LockUS
22 | XF:23IDA-VA:1{FS:1-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_03_Sts.LockDS
23 | XF:23IDA-VA:1{FS:1-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_03_Cmd.OpnCmd
24 | XF:23IDA-VA:1{FS:1-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_03_Cmd.ClsCmd
25 | XF:23IDA-VA:1{FS:1-GV:2} | Pos-Sts |  |  |  |  | GV_04_Sts.Sts
26 | XF:23IDA-VA:1{FS:1-GV:2} | Err-Sts |  |  |  |  | GV_04_Sts.StsFault
27 | XF:23IDA-VA:1{FS:1-GV:2} | Sts:FailOpn-Sts |  |  |  |  | GV_04_Sts.FailedToOpn
28 | XF:23IDA-VA:1{FS:1-GV:2} | Sts:FailCls-Sts |  |  |  |  | GV_04_Sts.FailedToCls
29 | XF:23IDA-VA:1{FS:1-GV:2} | Sts:US_Intlk-Sts |  |  |  |  | GV_04_Sts.LockUS
30 | XF:23IDA-VA:1{FS:1-GV:2} | Sts:DS_Intlk-Sts |  |  |  |  | GV_04_Sts.LockDS
31 | XF:23IDA-VA:1{FS:1-GV:2} | Cmd:Opn-Cmd |  |  |  |  | GV_04_Cmd.OpnCmd
32 | XF:23IDA-VA:1{FS:1-GV:2} | Cmd:Cls-Cmd |  |  |  |  | GV_04_Cmd.ClsCmd
33 | XF:23IDA-VA:2{Mir:1-GV:1} | Pos-Sts |  |  |  |  | GV_05_Sts.Sts
34 | XF:23IDA-VA:2{Mir:1-GV:1} | Err-Sts |  |  |  |  | GV_05_Sts.StsFault
35 | XF:23IDA-VA:2{Mir:1-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_05_Sts.FailedToOpn
36 | XF:23IDA-VA:2{Mir:1-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_05_Sts.FailedToCls
37 | XF:23IDA-VA:2{Mir:1-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_05_Sts.LockUS
38 | XF:23IDA-VA:2{Mir:1-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_05_Sts.LockDS
39 | XF:23IDA-VA:2{Mir:1-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_05_Cmd.OpnCmd
40 | XF:23IDA-VA:2{Mir:1-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_05_Cmd.ClsCmd
41 | XF:23IDA-VA:2{Mir:1-GV:2} | Pos-Sts |  |  |  |  | GV_06_Sts.Sts
42 | XF:23IDA-VA:2{Mir:1-GV:2} | Err-Sts |  |  |  |  | GV_06_Sts.StsFault
43 | XF:23IDA-VA:2{Mir:1-GV:2} | Sts:FailOpn-Sts |  |  |  |  | GV_06_Sts.FailedToOpn
44 | XF:23IDA-VA:2{Mir:1-GV:2} | Sts:FailCls-Sts |  |  |  |  | GV_06_Sts.FailedToCls
45 | XF:23IDA-VA:2{Mir:1-GV:2} | Sts:US_Intlk-Sts |  |  |  |  | GV_06_Sts.LockUS
46 | XF:23IDA-VA:2{Mir:1-GV:2} | Sts:DS_Intlk-Sts |  |  |  |  | GV_06_Sts.LockDS
47 | XF:23IDA-VA:2{Mir:1-GV:2} | Cmd:Opn-Cmd |  |  |  |  | GV_06_Cmd.OpnCmd
48 | XF:23IDA-VA:2{Mir:1-GV:2} | Cmd:Cls-Cmd |  |  |  |  | GV_06_Cmd.ClsCmd
49 | XF:23ID1-VA{Diag:01-GV:1} | Pos-Sts |  |  |  |  | GV_07_Sts.Sts
50 | XF:23ID1-VA{Diag:01-GV:1} | Err-Sts |  |  |  |  | GV_07_Sts.StsFault
51 | XF:23ID1-VA{Diag:01-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_07_Sts.FailedToOpn
52 | XF:23ID1-VA{Diag:01-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_07_Sts.FailedToCls
53 | XF:23ID1-VA{Diag:01-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_07_Sts.LockUS
54 | XF:23ID1-VA{Diag:01-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_07_Sts.LockDS
55 | XF:23ID1-VA{Diag:01-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_07_Cmd.OpnCmd
56 | XF:23ID1-VA{Diag:01-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_07_Cmd.ClsCmd
57 | XF:23ID1-VA{Diag:02-GV:1} | Pos-Sts |  |  |  |  | GV_08_Sts.Sts
58 | XF:23ID1-VA{Diag:02-GV:1} | Err-Sts |  |  |  |  | GV_08_Sts.StsFault
59 | XF:23ID1-VA{Diag:02-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_08_Sts.FailedToOpn
60 | XF:23ID1-VA{Diag:02-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_08_Sts.FailedToCls
61 | XF:23ID1-VA{Diag:02-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_08_Sts.LockUS
62 | XF:23ID1-VA{Diag:02-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_08_Sts.LockDS
63 | XF:23ID1-VA{Diag:02-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_08_Cmd.OpnCmd
64 | XF:23ID1-VA{Diag:02-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_08_Cmd.ClsCmd
65 | XF:23ID1-VA{Mon-GV:1} | Pos-Sts |  |  |  |  | GV_09_Sts.Sts
66 | XF:23ID1-VA{Mon-GV:1} | Err-Sts |  |  |  |  | GV_09_Sts.StsFault
67 | XF:23ID1-VA{Mon-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_09_Sts.FailedToOpn
68 | XF:23ID1-VA{Mon-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_09_Sts.FailedToCls
69 | XF:23ID1-VA{Mon-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_09_Sts.LockUS
70 | XF:23ID1-VA{Mon-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_09_Sts.LockDS
71 | XF:23ID1-VA{Mon-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_09_Cmd.OpnCmd
72 | XF:23ID1-VA{Mon-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_09_Cmd.ClsCmd
73 | XF:23ID1-VA{Slt:1-GV:1} | Pos-Sts |  |  |  |  | GV_10_Sts.Sts
74 | XF:23ID1-VA{Slt:1-GV:1} | Err-Sts |  |  |  |  | GV_10_Sts.StsFault
75 | XF:23ID1-VA{Slt:1-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_10_Sts.FailedToOpn
76 | XF:23ID1-VA{Slt:1-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_10_Sts.FailedToCls
77 | XF:23ID1-VA{Slt:1-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_10_Sts.LockUS
78 | XF:23ID1-VA{Slt:1-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_10_Sts.LockDS
79 | XF:23ID1-VA{Slt:1-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_10_Cmd.OpnCmd
80 | XF:23ID1-VA{Slt:1-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_10_Cmd.ClsCmd
81 | XF:23ID1-VA{Mir:3-GV:1} | Pos-Sts |  |  |  |  | GV_11_Sts.Sts
82 | XF:23ID1-VA{Mir:3-GV:1} | Err-Sts |  |  |  |  | GV_11_Sts.StsFault
83 | XF:23ID1-VA{Mir:3-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_11_Sts.FailedToOpn
84 | XF:23ID1-VA{Mir:3-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_11_Sts.FailedToCls
85 | XF:23ID1-VA{Mir:3-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_11_Sts.LockUS
86 | XF:23ID1-VA{Mir:3-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_11_Sts.LockDS
87 | XF:23ID1-VA{Mir:3-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_11_Cmd.OpnCmd
88 | XF:23ID1-VA{Mir:3-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_11_Cmd.ClsCmd
89 | XF:23ID1-VA{FV:1} | Pos-Sts |  |  |  |  | FV_01_Sts.Sts
90 | XF:23ID1-VA{FV:1} | Err-Sts |  |  |  |  | FV_01_Sts.StsFault
91 | XF:23ID1-VA{Diag:03-GV:1} | Pos-Sts |  |  |  |  | GV_12_Sts.Sts
92 | XF:23ID1-VA{Diag:03-GV:1} | Err-Sts |  |  |  |  | GV_12_Sts.StsFault
93 | XF:23ID1-VA{Diag:03-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_12_Sts.FailedToOpn
94 | XF:23ID1-VA{Diag:03-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_12_Sts.FailedToCls
95 | XF:23ID1-VA{Diag:03-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_12_Sts.LockUS
96 | XF:23ID1-VA{Diag:03-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_12_Sts.LockDS
97 | XF:23ID1-VA{Diag:03-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_12_Cmd.OpnCmd
98 | XF:23ID1-VA{Diag:03-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_12_Cmd.ClsCmd
99 | XF:23ID1-VA{PSh-GV:1} | Pos-Sts |  |  |  |  | GV_13_Sts.Sts
100 | XF:23ID1-VA{PSh-GV:1} | Err-Sts |  |  |  |  | GV_13_Sts.StsFault
101 | XF:23ID1-VA{PSh-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_13_Sts.FailedToOpn
102 | XF:23ID1-VA{PSh-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_13_Sts.FailedToCls
103 | XF:23ID1-VA{PSh-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_13_Sts.LockUS
104 | XF:23ID1-VA{PSh-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_13_Sts.LockDS
105 | XF:23ID1-VA{PSh-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_13_Cmd.OpnCmd
106 | XF:23ID1-VA{PSh-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_13_Cmd.ClsCmd
107 | XF:23ID1-VA{Diag:04-GV:1} | Pos-Sts |  |  |  |  | GV_14_Sts.Sts
108 | XF:23ID1-VA{Diag:04-GV:1} | Err-Sts |  |  |  |  | GV_14_Sts.StsFault
109 | XF:23ID1-VA{Diag:04-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_14_Sts.FailedToOpn
110 | XF:23ID1-VA{Diag:04-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_14_Sts.FailedToCls
111 | XF:23ID1-VA{Diag:04-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_14_Sts.LockUS
112 | XF:23ID1-VA{Diag:04-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_14_Sts.LockDS
113 | XF:23ID1-VA{Diag:04-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_14_Cmd.OpnCmd
114 | XF:23ID1-VA{Diag:04-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_14_Cmd.ClsCmd
115 | XF:23ID1-VA{DP:1-GV:1} | Pos-Sts |  |  |  |  | GV_15_Sts.Sts
116 | XF:23ID1-VA{DP:1-GV:1} | Err-Sts |  |  |  |  | GV_15_Sts.StsFault
117 | XF:23ID1-VA{DP:1-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_15_Sts.FailedToOpn
118 | XF:23ID1-VA{DP:1-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_15_Sts.FailedToCls
119 | XF:23ID1-VA{DP:1-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_15_Sts.LockUS
120 | XF:23ID1-VA{DP:1-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_15_Sts.LockDS
121 | XF:23ID1-VA{DP:1-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_15_Cmd.OpnCmd
122 | XF:23ID1-VA{DP:1-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_15_Cmd.ClsCmd
123 | XF:23ID1-VA{Diag:05-GV:1} | Pos-Sts |  |  |  |  | GV_16_Sts.Sts
124 | XF:23ID1-VA{Diag:05-GV:1} | Err-Sts |  |  |  |  | GV_16_Sts.StsFault
125 | XF:23ID1-VA{Diag:05-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_16_Sts.FailedToOpn
126 | XF:23ID1-VA{Diag:05-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_16_Sts.FailedToCls
127 | XF:23ID1-VA{Diag:05-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_16_Sts.LockUS
128 | XF:23ID1-VA{Diag:05-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_16_Sts.LockDS
129 | XF:23ID1-VA{Diag:05-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_16_Cmd.OpnCmd
130 | XF:23ID1-VA{Diag:05-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_16_Cmd.ClsCmd
131 | XF:23ID1-VA{Diag:06-GV:1} | Pos-Sts |  |  |  |  | GV_17_Sts.Sts
132 | XF:23ID1-VA{Diag:06-GV:1} | Err-Sts |  |  |  |  | GV_17_Sts.StsFault
133 | XF:23ID1-VA{Diag:06-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_17_Sts.FailedToOpn
134 | XF:23ID1-VA{Diag:06-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_17_Sts.FailedToCls
135 | XF:23ID1-VA{Diag:06-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_17_Sts.LockUS
136 | XF:23ID1-VA{Diag:06-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_17_Sts.LockDS
137 | XF:23ID1-VA{Diag:06-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_17_Cmd.OpnCmd
138 | XF:23ID1-VA{Diag:06-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_17_Cmd.ClsCmd
139 | XF:23ID2-VA{Diag:01-GV:1} | Pos-Sts |  |  |  |  | GV_18_Sts.Sts
140 | XF:23ID2-VA{Diag:01-GV:1} | Err-Sts |  |  |  |  | GV_18_Sts.StsFault
141 | XF:23ID2-VA{Diag:01-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_18_Sts.FailedToOpn
142 | XF:23ID2-VA{Diag:01-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_18_Sts.FailedToCls
143 | XF:23ID2-VA{Diag:01-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_18_Sts.LockUS
144 | XF:23ID2-VA{Diag:01-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_18_Sts.LockDS
145 | XF:23ID2-VA{Diag:01-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_18_Cmd.OpnCmd
146 | XF:23ID2-VA{Diag:01-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_18_Cmd.ClsCmd
147 | XF:23ID2-VA{Mon-GV:1} | Pos-Sts |  |  |  |  | GV_19_Sts.Sts
148 | XF:23ID2-VA{Mon-GV:1} | Err-Sts |  |  |  |  | GV_19_Sts.StsFault
149 | XF:23ID2-VA{Mon-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_19_Sts.FailedToOpn
150 | XF:23ID2-VA{Mon-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_19_Sts.FailedToCls
151 | XF:23ID2-VA{Mon-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_19_Sts.LockUS
152 | XF:23ID2-VA{Mon-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_19_Sts.LockDS
153 | XF:23ID2-VA{Mon-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_19_Cmd.OpnCmd
154 | XF:23ID2-VA{Mon-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_19_Cmd.ClsCmd
155 | XF:23ID2-VA{Slt:1-GV:1} | Pos-Sts |  |  |  |  | GV_20_Sts.Sts
156 | XF:23ID2-VA{Slt:1-GV:1} | Err-Sts |  |  |  |  | GV_20_Sts.StsFault
157 | XF:23ID2-VA{Slt:1-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_20_Sts.FailedToOpn
158 | XF:23ID2-VA{Slt:1-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_20_Sts.FailedToCls
159 | XF:23ID2-VA{Slt:1-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_20_Sts.LockUS
160 | XF:23ID2-VA{Slt:1-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_20_Sts.LockDS
161 | XF:23ID2-VA{Slt:1-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_20_Cmd.OpnCmd
162 | XF:23ID2-VA{Slt:1-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_20_Cmd.ClsCmd
163 | XF:23ID2-VA{FV:1} | Pos-Sts |  |  |  |  | FV_02_Sts.Sts
164 | XF:23ID2-VA{FV:1} | Err-Sts |  |  |  |  | FV_02_Sts.StsFault
165 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Pos-Sts |  |  |  |  | GV_21_Sts.Sts
166 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Err-Sts |  |  |  |  | GV_21_Sts.StsFault
167 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_21_Sts.FailedToOpn
168 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_21_Sts.FailedToCls
169 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_21_Sts.LockUS
170 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_21_Sts.LockDS
171 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_21_Cmd.OpnCmd
172 | XF:23ID2-VA{Pmp:Inl:01-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_21_Cmd.ClsCmd
173 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Pos-Sts |  |  |  |  | GV_22_Sts.Sts
174 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Err-Sts |  |  |  |  | GV_22_Sts.StsFault
175 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_22_Sts.FailedToOpn
176 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_22_Sts.FailedToCls
177 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_22_Sts.LockUS
178 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_22_Sts.LockDS
179 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_22_Cmd.OpnCmd
180 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_22_Cmd.ClsCmd
181 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Pos-Sts |  |  |  |  | GV_23_Sts.Sts
182 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Err-Sts |  |  |  |  | GV_23_Sts.StsFault
183 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_23_Sts.FailedToOpn
184 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_23_Sts.FailedToCls
185 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_23_Sts.LockUS
186 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_23_Sts.LockDS
187 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_23_Cmd.OpnCmd
188 | XF:23ID2-VA{Pmp:Inl:03-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_23_Cmd.ClsCmd
189 | XF:23ID2-VA{Diag:02-GV:1} | Pos-Sts |  |  |  |  | GV_24_Sts.Sts
190 | XF:23ID2-VA{Diag:02-GV:1} | Err-Sts |  |  |  |  | GV_24_Sts.StsFault
191 | XF:23ID2-VA{Diag:02-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_24_Sts.FailedToOpn
192 | XF:23ID2-VA{Diag:02-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_24_Sts.FailedToCls
193 | XF:23ID2-VA{Diag:02-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_24_Sts.LockUS
194 | XF:23ID2-VA{Diag:02-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_24_Sts.LockDS
195 | XF:23ID2-VA{Diag:02-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_24_Cmd.OpnCmd
196 | XF:23ID2-VA{Diag:02-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_24_Cmd.ClsCmd
197 | XF:23ID2-VA{Slt:2-GV:1} | Pos-Sts |  |  |  |  | GV_25_Sts.Sts
198 | XF:23ID2-VA{Slt:2-GV:1} | Err-Sts |  |  |  |  | GV_25_Sts.StsFault
199 | XF:23ID2-VA{Slt:2-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_25_Sts.FailedToOpn
200 | XF:23ID2-VA{Slt:2-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_25_Sts.FailedToCls
201 | XF:23ID2-VA{Slt:2-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_25_Sts.LockUS
202 | XF:23ID2-VA{Slt:2-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_25_Sts.LockDS
203 | XF:23ID2-VA{Slt:2-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_25_Cmd.OpnCmd
204 | XF:23ID2-VA{Slt:2-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_25_Cmd.ClsCmd
205 | XF:23ID2-VA{Chop-GV:1} | Pos-Sts |  |  |  |  | GV_26_Sts.Sts
206 | XF:23ID2-VA{Chop-GV:1} | Err-Sts |  |  |  |  | GV_26_Sts.StsFault
207 | XF:23ID2-VA{Chop-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_26_Sts.FailedToOpn
208 | XF:23ID2-VA{Chop-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_26_Sts.FailedToCls
209 | XF:23ID2-VA{Chop-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_26_Sts.LockUS
210 | XF:23ID2-VA{Chop-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_26_Sts.LockDS
211 | XF:23ID2-VA{Chop-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_26_Cmd.OpnCmd
212 | XF:23ID2-VA{Chop-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_26_Cmd.ClsCmd
213 | XF:23ID2-VA{Slt:3-GV:1} | Pos-Sts |  |  |  |  | GV_27_Sts.Sts
214 | XF:23ID2-VA{Slt:3-GV:1} | Err-Sts |  |  |  |  | GV_27_Sts.StsFault
215 | XF:23ID2-VA{Slt:3-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_27_Sts.FailedToOpn
216 | XF:23ID2-VA{Slt:3-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_27_Sts.FailedToCls
217 | XF:23ID2-VA{Slt:3-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_27_Sts.LockUS
218 | XF:23ID2-VA{Slt:3-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_27_Sts.LockDS
219 | XF:23ID2-VA{Slt:3-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_27_Cmd.OpnCmd
220 | XF:23ID2-VA{Slt:3-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_27_Cmd.ClsCmd
221 | XF:23ID2-VA{Mir:3-GV:1} | Pos-Sts |  |  |  |  | GV_28_Sts.Sts
222 | XF:23ID2-VA{Mir:3-GV:1} | Err-Sts |  |  |  |  | GV_28_Sts.StsFault
223 | XF:23ID2-VA{Mir:3-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_28_Sts.FailedToOpn
224 | XF:23ID2-VA{Mir:3-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_28_Sts.FailedToCls
225 | XF:23ID2-VA{Mir:3-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_28_Sts.LockUS
226 | XF:23ID2-VA{Mir:3-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_28_Sts.LockDS
227 | XF:23ID2-VA{Mir:3-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_28_Cmd.OpnCmd
228 | XF:23ID2-VA{Mir:3-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_28_Cmd.ClsCmd
229 | XF:23ID2-VA{Diag:03-GV:1} | Pos-Sts |  |  |  |  | GV_29_Sts.Sts
230 | XF:23ID2-VA{Diag:03-GV:1} | Err-Sts |  |  |  |  | GV_29_Sts.StsFault
231 | XF:23ID2-VA{Diag:03-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_29_Sts.FailedToOpn
232 | XF:23ID2-VA{Diag:03-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_29_Sts.FailedToCls
233 | XF:23ID2-VA{Diag:03-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_29_Sts.LockUS
234 | XF:23ID2-VA{Diag:03-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_29_Sts.LockDS
235 | XF:23ID2-VA{Diag:03-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_29_Cmd.OpnCmd
236 | XF:23ID2-VA{Diag:03-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_29_Cmd.ClsCmd
237 | XF:23ID2-VA{GC-GV:1} | Pos-Sts |  |  |  |  | GV_30_Sts.Sts
238 | XF:23ID2-VA{GC-GV:1} | Err-Sts |  |  |  |  | GV_30_Sts.StsFault
239 | XF:23ID2-VA{GC-GV:1} | Sts:FailOpn-Sts |  |  |  |  | GV_30_Sts.FailedToOpn
240 | XF:23ID2-VA{GC-GV:1} | Sts:FailCls-Sts |  |  |  |  | GV_30_Sts.FailedToCls
241 | XF:23ID2-VA{GC-GV:1} | Sts:US_Intlk-Sts |  |  |  |  | GV_30_Sts.LockUS
242 | XF:23ID2-VA{GC-GV:1} | Sts:DS_Intlk-Sts |  |  |  |  | GV_30_Sts.LockDS
243 | XF:23ID2-VA{GC-GV:1} | Cmd:Opn-Cmd |  |  |  |  | GV_30_Cmd.OpnCmd
244 | XF:23ID2-VA{GC-GV:1} | Cmd:Cls-Cmd |  |  |  |  | GV_30_Cmd.ClsCmd
245 | XF:23ID2-VA{GC-GV:2} | Pos-Sts |  |  |  |  | GV_31_Sts.Sts
246 | XF:23ID2-VA{GC-GV:2} | Err-Sts |  |  |  |  | GV_31_Sts.StsFault
247 | XF:23ID2-VA{GC-GV:2} | Sts:FailOpn-Sts |  |  |  |  | GV_31_Sts.FailedToOpn
248 | XF:23ID2-VA{GC-GV:2} | Sts:FailCls-Sts |  |  |  |  | GV_31_Sts.FailedToCls
249 | XF:23ID2-VA{GC-GV:2} | Sts:US_Intlk-Sts |  |  |  |  | GV_31_Sts.LockUS
250 | XF:23ID2-VA{GC-GV:2} | Sts:DS_Intlk-Sts |  |  |  |  | GV_31_Sts.LockDS
251 | XF:23ID2-VA{GC-GV:2} | Cmd:Opn-Cmd |  |  |  |  | GV_31_Cmd.OpnCmd
252 | XF:23ID2-VA{GC-GV:2} | Cmd:Cls-Cmd |  |  |  |  | GV_31_Cmd.ClsCmd
253 | XF:23ID2-VA{GC-GV:3} | Pos-Sts |  |  |  |  | GV_32_Sts.Sts
254 | XF:23ID2-VA{GC-GV:3} | Err-Sts |  |  |  |  | GV_32_Sts.StsFault
255 | XF:23ID2-VA{GC-GV:3} | Sts:FailOpn-Sts |  |  |  |  | GV_32_Sts.FailedToOpn
256 | XF:23ID2-VA{GC-GV:3} | Sts:FailCls-Sts |  |  |  |  | GV_32_Sts.FailedToCls
257 | XF:23ID2-VA{GC-GV:3} | Sts:US_Intlk-Sts |  |  |  |  | GV_32_Sts.LockUS
258 | XF:23ID2-VA{GC-GV:3} | Sts:DS_Intlk-Sts |  |  |  |  | GV_32_Sts.LockDS
259 | XF:23ID2-VA{GC-GV:3} | Cmd:Opn-Cmd |  |  |  |  | GV_32_Cmd.OpnCmd
260 | XF:23ID2-VA{GC-GV:3} | Cmd:Cls-Cmd |  |  |  |  | GV_32_Cmd.ClsCmd
| XF:23ID-PPS{Sh:FE} | Pos-Sts |  |  |  |  | FE_SH_Sts.Sts
| XF:23ID-PPS{Sh:FE} | Err-Sts |  |  |  |  | FE_SH_Sts.StsFault
| XF:23ID-PPS{Sh:FE} | Sts:FailOpn-Sts |  |  |  |  | FE_SH_Sts.FailedToOpn
| XF:23ID-PPS{Sh:FE} | Sts:FailCls-Sts |  |  |  |  | FE_SH_Sts.FailedToCls
| XF:23ID-PPS{Sh:FE} | Sts:Permit-Sts |  |  |  |  | FE_SH_Sts.LockUS
| XF:23IDA-PPS:1{PSh} | Pos-Sts |  |  |  |  | SH1_Sts.Sts
| XF:23IDA-PPS:1{PSh} | Err-Sts |  |  |  |  | SH1_Sts.StsFault
| XF:23IDA-PPS:1{PSh} | Sts:FailOpn-Sts |  |  |  |  | SH1_Sts.FailedToOpn
| XF:23IDA-PPS:1{PSh} | Sts:FailCls-Sts |  |  |  |  | SH1_Sts.FailedToCls
| XF:23IDA-PPS:1{PSh} | Sts:Permit-Sts |  |  |  |  | SH1_Sts.LockUS
| XF:23IDA-PPS:2{PSh} | Pos-Sts |  |  |  |  | SH2_Sts.Sts
| XF:23IDA-PPS:2{PSh} | Err-Sts |  |  |  |  | SH2_Sts.StsFault
| XF:23IDA-PPS:2{PSh} | Sts:FailOpn-Sts |  |  |  |  | SH2_Sts.FailedToOpn
| XF:23IDA-PPS:2{PSh} | Sts:FailCls-Sts |  |  |  |  | SH2_Sts.FailedToCls
| XF:23IDA-PPS:2{PSh} | Sts:Permit-Sts |  |  |  |  | SH2_Sts.LockUS
| XF:23ID1-PPS{PSh} | Pos-Sts |  |  |  |  | SH3_Sts.Sts
| XF:23ID1-PPS{PSh} | Err-Sts |  |  |  |  | SH3_Sts.StsFault
| XF:23ID1-PPS{PSh} | Sts:FailOpn-Sts |  |  |  |  | SH3_Sts.FailedToOpn
| XF:23ID1-PPS{PSh} | Sts:FailCls-Sts |  |  |  |  | SH3_Sts.FailedToCls
| XF:23ID1-PPS{PSh} | Sts:Permit-Sts |  |  |  |  | SH3_Sts.LockUS
| XF:23ID2-PPS{PSh} | Pos-Sts |  |  |  |  | SH4_Sts.Sts
| XF:23ID2-PPS{PSh} | Err-Sts |  |  |  |  | SH4_Sts.StsFault
| XF:23ID2-PPS{PSh} | Sts:FailOpn-Sts |  |  |  |  | SH4_Sts.FailedToOpn
| XF:23ID2-PPS{PSh} | Sts:FailCls-Sts |  |  |  |  | SH4_Sts.FailedToCls
| XF:23ID2-PPS{PSh} | Sts:Permit-Sts |  |  |  |  | SH4_Sts.LockUS
261 | XF:23IDA-VA:0{DP:1} | F-Sts |  |  |  |  | F_Sts[0]
262 | XF:23IDA-OP:1{Mir:1} | F-Sts |  |  |  |  | F_Sts[1]
263 | XF:23IDA-OP:1{Mir:1-Msk} | F-Sts |  |  |  |  | F_Sts[2]
264 | XF:23IDA-OP:2{Mir:1A} | F-Sts |  |  |  |  | F_Sts[3]
265 | XF:23IDA-OP:2{Mir:1-Msk} | F-Sts |  |  |  |  | F_Sts[4]
266 | XF:23IDA-OP:1{FS:1} | F-Sts |  |  |  |  | F_Sts[5]
267 | XF:23IDA-OP:2{Mir:1B} | F-Sts |  |  |  |  | F_Sts[6]
268 | XF:23ID1-OP{Mon-Mir} | F-Sts |  |  |  |  | F_Sts[7]
269 | XF:23ID1-OP{Mon-Grt} | F-Sts |  |  |  |  | F_Sts[8]
270 | XF:23ID1-OP{Diag:02} | F-Sts |  |  |  |  | F_Sts[9]
271 | XF:23ID2-OP{Mon-Mir} | F-Sts |  |  |  |  | F_Sts[10]
272 | XF:23ID2-OP{Mon-Grt} | F-Sts |  |  |  |  | F_Sts[11]
273 | XF:23ID2-OP{Diag:01} | F-Sts |  |  |  |  | F_Sts[12]
274 | XF:23IDA-OP:0{Msk:1} | F-Sts |  |  |  |  | F_Sts[13]
275 | XF:23IDA-OP:1{Msk:1} | F-Sts |  |  |  |  | F_Sts[14]
276 | XF:23IDA-OP:2{Msk:1} | F-Sts |  |  |  |  | F_Sts[15]
277 | XF:23IDA-OP:1{PSh} | F-Sts |  |  |  |  | F_Sts[16]
278 | XF:23IDA-OP:2{PSh} | F-Sts |  |  |  |  | F_Sts[17]
279 | XF:23ID1-OP{Mon-Msk} | F-Sts |  |  |  |  | F_Sts[18]
280 | XF:23ID2-OP{Mon-Msk} | F-Sts |  |  |  |  | F_Sts[19]
281 | XF:23IDA-UT{Circuit:1} | F-Sts |  |  |  |  | F_Sts[20]
282 | XF:23IDA-UT{Circuit:10} | F-Sts |  |  |  |  | F_Sts[21]
283 | XF:23IDA-UT{DI} | F-Sts |  |  |  |  | F_Sts[22]
284 | XF:23IDA-UT{DI} | P:Supply-Sts |  |  |  |  | F_Sts[23]
285 | XF:23IDA-UT{DI} | P:Return-Sts |  |  |  |  | F_Sts[24]
286 | XF:23ID1-UT{DI} | P:Supply-Sts |  |  |  |  | F_Sts[25]
287 | XF:23ID1-UT{DI} | P:Return-Sts |  |  |  |  | F_Sts[26]
288 | XF:23IDA-OP:0{Msk:1} | T:1-Sts |  |  |  |  | IDA_T_Sts[0]
289 | XF:23IDA-OP:0{Msk:1} | T:2-Sts |  |  |  |  | IDA_T_Sts[1]
290 | XF:23IDA-OP:1{Mir:1-Msk} | T:1-Sts |  |  |  |  | IDA_T_Sts[2]
291 | XF:23IDA-OP:1{Mir:1-Msk} | T:2-Sts |  |  |  |  | IDA_T_Sts[3]
292 | XF:23IDA-OP:1{Mir:1} | T:1-Sts |  |  |  |  | IDA_T_Sts[4]
293 | XF:23IDA-OP:1{Mir:1} | T:2-Sts |  |  |  |  | IDA_T_Sts[5]
294 | XF:23IDA-OP:1{Msk:1} | T:1-Sts |  |  |  |  | IDA_T_Sts[6]
295 | XF:23IDA-OP:1{Msk:1} | T:2-Sts |  |  |  |  | IDA_T_Sts[7]
296 | XF:23IDA-OP:1{FS:1} | T-Sts |  |  |  |  | IDA_T_Sts[8]
297 | XF:23IDA-OP:2{Mir:1A-Msk} | T:1-Sts |  |  |  |  | IDA_T_Sts[9]
298 | XF:23IDA-OP:2{Mir:1B-Msk} | T:1-Sts |  |  |  |  | IDA_T_Sts[10]
299 | XF:23IDA-OP:2{Mir:1A} | T:1-Sts |  |  |  |  | IDA_T_Sts[11]
300 | XF:23IDA-OP:2{Mir:1B} | T:1-Sts |  |  |  |  | IDA_T_Sts[12]
301 | XF:23IDA-OP:2{Mir:1A-Msk} | T:2-Sts |  |  |  |  | IDA_T_Sts[13]
302 | XF:23IDA-OP:2{Mir:1B-Msk} | T:2-Sts |  |  |  |  | IDA_T_Sts[14]
303 | XF:23IDA-OP:2{Mir:1A} | T:2-Sts |  |  |  |  | IDA_T_Sts[15]
304 | XF:23IDA-OP:2{Mir:1B} | T:2-Sts |  |  |  |  | IDA_T_Sts[16]
305 | XF:23IDA-OP:2{Msk:1} | T:1-Sts |  |  |  |  | IDA_T_Sts[17]
306 | XF:23IDA-OP:2{Msk:1} | T:2-Sts |  |  |  |  | IDA_T_Sts[18]
307 | XF:23IDA-VA:0{DP:1} | T-Sts |  |  |  |  | IDA_T_Sts[19]
308 | XF:23IDA-UT{DI} | T:Supply-Sts |  |  |  |  | IDA_T_Sts[20]
309 | XF:23IDA-UT{DI} | T:Return-Sts |  |  |  |  | IDA_T_Sts[21]
310 | XF:23IDA-UT{PCW} | T:Supply-Sts |  |  |  |  | IDA_T_Sts[22]
311 | XF:23IDA-UT{PCW} | T:Return-Sts |  |  |  |  | IDA_T_Sts[23]
312 | XF:23ID1-OP{Diag:02} | T-Sts |  |  |  |  | ID1_T_Sts[0]
313 | XF:23ID1-OP{Mon-Mir} | T-Sts |  |  |  |  | ID1_T_Sts[1]
314 | XF:23ID1-OP{Mon-Mir:Msk} | T-Sts |  |  |  |  | ID1_T_Sts[2]
315 | XF:23ID1-OP{Mon-Grt:1} | T-Sts |  |  |  |  | ID1_T_Sts[3]
316 | XF:23ID1-OP{Mon-Grt:2} | T-Sts |  |  |  |  | ID1_T_Sts[4]
317 | XF:23ID1-OP{Mon-Grt:3} | T-Sts |  |  |  |  | ID1_T_Sts[5]
318 | XF:23ID1-OP{Mon-Grt:4} | T-Sts |  |  |  |  | ID1_T_Sts[6]
319 | XF:23ID1-OP{Mir:3-Bdr} | T-Sts |  |  |  |  | ID1_T_Sts[7]
320 | XF:23ID2-OP{Diag:01} | T-Sts |  |  |  |  | ID2_T_Sts[0]
321 | XF:23ID2-OP{Mon-Mir} | T-Sts |  |  |  |  | ID2_T_Sts[1]
322 | XF:23ID2-OP{Mon-Mir:Msk} | T-Sts |  |  |  |  | ID2_T_Sts[2]
323 | XF:23ID2-OP{Mon-Grt:1} | T-Sts |  |  |  |  | ID2_T_Sts[3]
| XF:23ID2-OP{Mon-Grt:2} | T-Sts |  |  |  |  | ID2_T_Sts[4]
| XF:23ID2-OP{Mon-Grt:3} | T-Sts |  |  |  |  | ID2_T_Sts[5]
| XF:23ID2-OP{Mon-Grt:4} | T-Sts |  |  |  |  | ID2_T_Sts[6]
| XF:23ID2-OP{Chop} | T-Sts |  |  |  |  | ID2_T_Sts[7]
XF:23ID-PPS{Sh:FE}Cmd:Open-Cmd
XF:23ID-PPS{Sh:FE}Cmd:Close-Cmd
XF:23IDA-PPS:1{PSh}Cmd:Open-Cmd
XF:23IDA-PPS:1{PSh}Cmd:Close-Cmd
XF:23IDA-PPS:2{PSh}Cmd:Open-Cmd
XF:23IDA-PPS:2{PSh}Cmd:Close-Cmd
XF:23ID1-PPS{PSh}Cmd:Open-Cmd
XF:23ID1-PPS{PSh}Cmd:Close-Cmd
XF:23ID2-PPS{PSh}Cmd:Open-Cmd
XF:23ID2-PPS{PSh}Cmd:Close-Cmd
| XF:23IDA-UT{DI-Vlv:Supply} | Pos-Sts |  |  |  |  | FOE_Sply_Sts.Sts
| XF:23IDA-UT{DI-Vlv:Supply} | Err-Sts |  |  |  |  | FOE_Sply_Sts.StsFault
| XF:23IDA-UT{DI-Vlv:Supply} | Sts:FailOpn-Sts |  |  |  |  | FOE_Sply_Sts.FailedToOpn
| XF:23IDA-UT{DI-Vlv:Supply} | Sts:FailCls-Sts |  |  |  |  | FOE_Sply_Sts.FailedToCls
| XF:23IDA-UT{DI-Vlv:Supply} | Cmd:Opn-Cmd |  |  |  |  | FOE_Sply_Cmd.OpnCmd
| XF:23IDA-UT{DI-Vlv:Supply} | Cmd:Cls-Cmd |  |  |  |  | FOE_Sply_Cmd.ClsCmd
| XF:23IDA-UT{DI-Vlv:Return} | Pos-Sts |  |  |  |  | FOE_Rtrn_Sts.Sts
| XF:23IDA-UT{DI-Vlv:Return} | Err-Sts |  |  |  |  | FOE_Rtrn_Sts.StsFault
| XF:23IDA-UT{DI-Vlv:Return} | Sts:FailOpn-Sts |  |  |  |  | FOE_Rtrn_Sts.FailedToOpn
| XF:23IDA-UT{DI-Vlv:Return} | Sts:FailCls-Sts |  |  |  |  | FOE_Rtrn_Sts.FailedToCls
| XF:23IDA-UT{DI-Vlv:Return} | Cmd:Opn-Cmd |  |  |  |  | FOE_Rtrn_Cmd.OpnCmd
| XF:23IDA-UT{DI-Vlv:Return} | Cmd:Cls-Cmd |  |  |  |  | FOE_Rtrn_Cmd.ClsCmd
| XF:23ID-UT{PCW-Vlv:Supply} | Pos-Sts |  |  |  |  | Floor_Sply_Sts.Sts
| XF:23ID-UT{PCW-Vlv:Supply} | Err-Sts |  |  |  |  | Floor_Sply_Sts.StsFault
| XF:23ID-UT{PCW-Vlv:Supply} | Sts:FailOpn-Sts |  |  |  |  | Floor_Sply_Sts.FailedToOpn
| XF:23ID-UT{PCW-Vlv:Supply} | Sts:FailCls-Sts |  |  |  |  | Floor_Sply_Sts.FailedToCls
| XF:23ID-UT{PCW-Vlv:Supply} | Cmd:Opn-Cmd |  |  |  |  | Floor_Sply_Cmd.OpnCmd
| XF:23ID-UT{PCW-Vlv:Supply} | Cmd:Cls-Cmd |  |  |  |  | Floor_Sply_Cmd.ClsCmd
| XF:23ID-UT{PCW-Vlv:Return} | Pos-Sts |  |  |  |  | Floor_Rtrn_Sts.Sts
| XF:23ID-UT{PCW-Vlv:Return} | Err-Sts |  |  |  |  | Floor_Rtrn_Sts.StsFault
| XF:23ID-UT{PCW-Vlv:Return} | Sts:FailOpn-Sts |  |  |  |  | Floor_Rtrn_Sts.FailedToOpn
| XF:23ID-UT{PCW-Vlv:Return} | Sts:FailCls-Sts |  |  |  |  | Floor_Rtrn_Sts.FailedToCls
| XF:23ID-UT{PCW-Vlv:Return} | Cmd:Opn-Cmd |  |  |  |  | Floor_Rtrn_Cmd.OpnCmd
| XF:23ID-UT{PCW-Vlv:Return} | Cmd:Cls-Cmd |  |  |  |  | Floor_Rtrn_Cmd.ClsCmd
| XF:23ID-PPS{Sh:FE} | Alrm-Sts |  |  |  |  | PPS_Sts[22]
| XF:23IDA-PPS:1{PSh} | Alrm-Sts |  |  |  |  | PPS_Sts[23]
| XF:23IDA-PPS:2{PSh} | Alrm-Sts |  |  |  |  | PPS_Sts[24]
| XF:23ID1-PPS{PSh} | Alrm-Sts |  |  |  |  | PPS_Sts[25]
| XF:23ID2-PPS{PSh} | Alrm-Sts |  |  |  |  | PPS_Sts[26]

## EPICS db Base
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-VA:0{DP:1-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-VA:0{DP:1-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_01_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{Mir:1-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-VA:1{Mir:1-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-VA:1{Mir:1-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_02_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-VA:1{FS:1-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-VA:1{FS:1-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_03_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:1{FS:1-GV:2}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-VA:1{FS:1-GV:2}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-VA:1{FS:1-GV:2}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_04_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-VA:2{Mir:1-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-VA:2{Mir:1-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_05_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:2{Mir:1-GV:2}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-VA:2{Mir:1-GV:2}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-VA:2{Mir:1-GV:2}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_06_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:01-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:01-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:01-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_07_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:02-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:02-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:02-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_08_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mon-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Mon-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Mon-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_09_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Slt:1-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Slt:1-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Slt:1-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_10_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Mir:3-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Mir:3-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Mir:3-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_11_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_01_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{FV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_01_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:03-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:03-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:03-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_12_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{PSh-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{PSh-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{PSh-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_13_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:04-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:04-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:04-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_14_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{DP:1-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{DP:1-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{DP:1-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_15_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:05-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:05-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:05-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_16_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-VA{Diag:06-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:06-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-VA{Diag:06-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_17_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:01-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Diag:01-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Diag:01-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_18_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mon-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Mon-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Mon-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_19_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:1-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Slt:1-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Slt:1-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_20_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_02_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{FV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FV_02_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Pmp:Inl:01-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_21_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Pmp:Inl:02-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_22_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Pmp:Inl:03-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_23_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:02-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Diag:02-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Diag:02-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_24_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:2-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Slt:2-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Slt:2-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_25_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Chop-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Chop-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Chop-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_26_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Slt:3-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Slt:3-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Slt:3-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_27_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Mir:3-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Mir:3-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Mir:3-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_28_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{Diag:03-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Diag:03-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{Diag:03-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_29_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:1}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{GC-GV:1}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{GC-GV:1}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_30_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:2}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{GC-GV:2}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{GC-GV:2}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_31_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Sts:US_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-VA{GC-GV:3}Sts:DS_Intlk-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Sts.LockDS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID2-VA{GC-GV:3}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-VA{GC-GV:3}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | GV_32_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FE_SH_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FE_SH_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FE_SH_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FE_SH_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Sts:Permit-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FE_SH_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH1_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH1_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH1_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH1_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Sts:Permit-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH1_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH2_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH2_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH2_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH2_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Sts:Permit-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH2_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH3_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH3_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH3_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH3_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Sts:Permit-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH3_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH4_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH4_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH4_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH4_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Sts:Permit-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | SH4_Sts.LockUS | S 0.5 | ")NL | field( | ZNAM | , " | Interlocked | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[0] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[1] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1-Msk}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[2] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[3] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1-Msk}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[4] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{FS:1}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[5] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[6] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Mir}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[7] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[8] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Diag:02}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[9] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Mir}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[10] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[11] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Diag:01}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[12] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:0{Msk:1}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[13] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Msk:1}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[14] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Msk:1}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[15] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{PSh}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[16] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{PSh}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[17] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Msk}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[18] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Msk}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[19] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{Circuit:1}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[20] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL |  |  |  |  | ")NL}NL
record( | bi | , " | XF:23IDA-UT{Circuit:10}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[21] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL |  |  |  |  | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}F-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[22] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}P:Supply-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[23] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}P:Return-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[24] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-UT{DI}P:Supply-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[25] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-UT{DI}P:Return-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | F_Sts[26] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:0{Msk:1}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[0] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:0{Msk:1}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[1] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1-Msk}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[2] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1-Msk}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[3] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[4] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Mir:1}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[5] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Msk:1}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[6] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{Msk:1}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[7] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:1{FS:1}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[8] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A-Msk}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[9] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B-Msk}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[10] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[11] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[12] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A-Msk}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[13] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B-Msk}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[14] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1A}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[15] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Mir:1B}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[16] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Msk:1}T:1-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[17] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-OP:2{Msk:1}T:2-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[18] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-VA:0{DP:1}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[19] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}T:Supply-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[20] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI}T:Return-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[21] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{PCW}T:Supply-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[22] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{PCW}T:Return-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | IDA_T_Sts[23] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Diag:02}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[0] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Mir}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[1] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Mir:Msk}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[2] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:1}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[3] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:2}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[4] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:3}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[5] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mon-Grt:4}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[6] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-OP{Mir:3-Bdr}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID1_T_Sts[7] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Diag:01}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[0] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Mir}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[1] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Mir:Msk}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[2] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:1}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[3] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:2}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[4] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:3}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[5] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Mon-Grt:4}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[6] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-OP{Chop}T-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | ID2_T_Sts[7] | S 0.5 | ")NL | field( | ZNAM | , " | Interlock | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID-PPS{Sh:FE}Cmd:Open-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | FESh_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID-PPS{Sh:FE}Cmd:Close-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | FESh_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-PPS:1{PSh}Cmd:Open-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh1_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-PPS:1{PSh}Cmd:Close-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh1_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-PPS{PSh}Cmd:Open-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh2_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-PPS{PSh}Cmd:Close-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh2_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-PPS{PSh}Cmd:Open-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh3_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID1-PPS{PSh}Cmd:Close-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh3_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-PPS{PSh}Cmd:Open-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh4_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID2-PPS{PSh}Cmd:Close-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | SSh4_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Supply}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Supply}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Supply}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Supply}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-UT{DI-Vlv:Supply}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-UT{DI-Vlv:Supply}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | FOE_Sply_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Return}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Return}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Return}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-UT{DI-Vlv:Return}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23IDA-UT{DI-Vlv:Return}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23IDA-UT{DI-Vlv:Return}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | FOE_Rtrn_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Supply}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Supply}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Supply}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Supply}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID-UT{PCW-Vlv:Supply}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID-UT{PCW-Vlv:Supply}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | Floor_Sply_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Return}Pos-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Sts.Sts | S 0.5 | ")NL | field( | ZNAM | , " | Closed | ")NL | field( | ONAM | , " | Open | ")NL | field( | ZSV | , " | MINOR | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Return}Err-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Sts.StsFault | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Return}Sts:FailOpn-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Sts.FailedToOpn | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID-UT{PCW-Vlv:Return}Sts:FailCls-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Sts.FailedToCls | S 0.5 | ")NL | field( | ZNAM | , " | ERROR | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bo | , " | XF:23ID-UT{PCW-Vlv:Return}Cmd:Opn-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Cmd.OpnCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bo | , " | XF:23ID-UT{PCW-Vlv:Return}Cmd:Cls-Cmd | ")NL{NL | field( | SCAN | , " | Passive | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | OUT | , " | @XF_23ID_EPS_PLC_A2 | Floor_Rtrn_Cmd.ClsCmd | S 0.5 | [15 empty] | ")NL}NL
record( | bi | , " | XF:23ID-PPS{Sh:FE}Alrm-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PPS_Sts[22] | S 0.5 | ")NL | field( | ZNAM | , " | ALARM | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:1{PSh}Alrm-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PPS_Sts[23] | S 0.5 | ")NL | field( | ZNAM | , " | ALARM | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23IDA-PPS:2{PSh}Alrm-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PPS_Sts[24] | S 0.5 | ")NL | field( | ZNAM | , " | ALARM | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID1-PPS{PSh}Alrm-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PPS_Sts[25] | S 0.5 | ")NL | field( | ZNAM | , " | ALARM | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL
record( | bi | , " | XF:23ID2-PPS{PSh}Alrm-Sts | ")NL{NL | field( | SCAN | , " | I/O Intr | ")NL | field( | DTYP | , " | EtherIP | ")NL | field( | INP | , " | @XF_23ID_EPS_PLC_A2 | PPS_Sts[26] | S 0.5 | ")NL | field( | ZNAM | , " | ALARM | ")NL | field( | ONAM | , " | OK | ")NL | field( | ZSV | , " | MAJOR | ")NL}NL

## v1
Stimulus | Check 1 | Check 2 | Check 3 | Check 4 | Check 5 | Check 6
XF:23IDA-VA:0{Diag:1-CCG:1} | XF:23IDA-VA:0{DP:1-GV:1} | FE SHUTTER | Vacuum Good Signal to FE
XF:23IDA-VA:0{Diag:1-IP:1} | XF:23IDA-VA:0{DP:1-GV:1} | FE SHUTTER | Vacuum Good Signal to FE
XF:23IDA-VA:0{Msk:1-CCG:1} | XF:23IDA-VA:0{DP:1-GV:1} | FE SHUTTER | Vacuum Good Signal to FE
XF:23IDA-VA:0{Msk:1-IP:1} | XF:23IDA-VA:0{DP:1-GV:1} | FE SHUTTER | Vacuum Good Signal to FE
XF:23IDA-VA:0{DP:1-IP:1} | XF:23IDA-VA:0{DP:1-GV:1} | FE SHUTTER | Vacuum Good Signal to FE
XF:23IDA-VA:1{Mir:1-CCG:1} | XF:23IDA-VA:0{DP:1-GV:1} | XF:23IDA-VA:1{Mir:1-GV:1} | FE SHUTTER | Vacuum Good Signal to FE
XF:23IDA-VA:1{Mir:1-IP:1} | XF:23IDA-VA:0{DP:1-GV:1} | XF:23IDA-VA:1{Mir:1-GV:1} | FE SHUTTER | Vacuum Good Signal to FE
XF:23IDA-VA:0{Diag:1-TCG:1} | XF:23IDA-VA:0{DP:1-GV:1} | Vacuum Good Signal to FE
XF:23IDA-VA:0{Msk:1-TCG:1} | XF:23IDA-VA:0{DP:1-GV:1} | Vacuum Good Signal to FE
XF:23IDA-VA:1{Mir:1-TCG:1} | XF:23IDA-VA:0{DP:1-GV:1} | XF:23IDA-VA:1{Mir:1-GV:1} | Vacuum Good Signal to FE
REQUEST XF:23IDA-VA:0{DP:1-GV:1} | XF:23IDA-VA:0{DP:1-GV:1}
XF:23IDA-VA:1{FS:1-CCG:1} | XF:23IDA-VA:1{Mir:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1} | FE SHUTTER | XF:23IDA-VA:1{FS:1-GV:2} | XF:23IDA-VA:0{DP:1-GV:1}
XF:23IDA-VA:1{FS:1-IP:1} | XF:23IDA-VA:1{Mir:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1} | FE SHUTTER | XF:23IDA-VA:1{FS:1-GV:2} | XF:23IDA-VA:0{DP:1-GV:1}
XF:23IDA-VA:1{FS:1-TCG:1} | XF:23IDA-VA:1{Mir:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
REQUEST XF:23IDA-VA:1{Mir:1-GV:1} | XF:23IDA-VA:1{Mir:1-GV:1}
XF:23IDA-VA:2{Mir:1-CCG:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:2} | XF:23IDA-VA:1{Mir:1-GV:1}
XF:23IDA-VA:2{Mir:1-IP:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:2} | XF:23IDA-VA:1{Mir:1-GV:1}
XF:23IDA-VA:2{Mir:1-TCG:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:2}
REQUEST XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1}
REQUEST XF:23IDA-VA:1{FS:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23IDA:VA:1{SSh:1-CCG:1} | XF:23IDA-VA:2{Mir:1-GV:1}
XF:23IDA:VA:1{SSh:1-IP:1} | XF:23IDA-VA:2{Mir:1-GV:1}
XF:23ID1:VA{Diag:1-CCG:1} | XF:23IDA-VA:2{Mir:1-GV:1}
XF:23ID1:VA{Diag:1-IP:1} | XF:23IDA-VA:2{Mir:1-GV:1}
REQUEST XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:1}
XF:23IDA:VA:2{SSh:1-CCG:1} | XF:23IDA-VA:2{Mir:1-GV:2}
XF:23IDA:VA:2{SSh:1-IP:1} | XF:23IDA-VA:2{Mir:1-GV:2}
XF:23ID2:VA{Diag:1-CCG:1} | XF:23IDA-VA:2{Mir:1-GV:2}
XF:23ID2:VA{Diag:1-IP:1} | XF:23IDA-VA:2{Mir:1-GV:2}
REQUEST XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:2{Mir:1-GV:2}
XF:23ID1-VA{Diag:01-CCG:1} | XF:23ID1-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23ID1-VA{Diag:01-IP:1} | XF:23ID1-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23IDA-VA:1{SSh:1-CCG:1} | XF:23ID1-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23IDA-VA:1{SSh:1-IP:1} | XF:23ID1-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23ID1-VA{Diag:02-CCG:1} | XF:23ID1-VA{Diag:01-GV:1} | XF:23ID1-VA{Diag:02-GV:1} | SHUTTER 1 | XF:23IDA-VA:2{Mir:1-GV:1}
XF:23ID1-VA{Diag:02-IP:1} | XF:23ID1-VA{Diag:01-GV:1} | XF:23ID1-VA{Diag:02-GV:1} | SHUTTER 1 | XF:23IDA-VA:2{Mir:1-GV:1}
XF:23ID1-VA{Diag:01-TCG:1} | XF:23ID1-VA{Diag:01-GV:1}
XF:23IDA-VA:1{SSh:1-TCG:1} | XF:23ID1-VA{Diag:01-GV:1}
XF:23ID1-VA{Diag:02-TCG:1} | XF:23ID1-VA{Diag:01-GV:1} | XF:23ID1-VA{Diag:02-GV:1}
REQUEST XF:23ID1-VA{Diag:01-GV:1 | XF:23ID1-VA{Diag:01-GV:1}
XF:23ID1-VA{Mon-CCG:1} | XF:23ID1-VA{Diag:02-GV:1} | XF:23ID1-VA{Mon-GV:1} | SHUTTER 1 | XF:23ID1-VA{Diag:1-GV:1}
XF:23ID1-VA{Mon-IP:1} | XF:23ID1-VA{Diag:02-GV:1} | XF:23ID1-VA{Mon-GV:1} | SHUTTER 1 | XF:23ID1-VA{Diag:1-GV:1}
XF:23ID1-VA{Mon-TCG:1} | XF:23ID1-VA{Diag:02-GV:1} | XF:23ID1-VA{Mon-GV:1}
REQUEST XF:23ID1-VA{Diag:02-GV:1} | XF:23ID1-VA{Diag:02-GV:1}
XF:23ID1-VA{Slt:1-CCG:1} | XF:23ID1-VA{Mon-GV:1} | XF:23ID1-VA{Slt:1-GV:1} | SHUTTER 1 | XF:23ID1-VA{Diag:2-GV:1}
XF:23ID1-VA{Slt:1-IP:1} | XF:23ID1-VA{Mon-GV:1} | XF:23ID1-VA{Slt:1-GV:1} | SHUTTER 1 | XF:23ID1-VA{Diag:2-GV:1}
XF:23ID1-VA{Slt:1-TCG:1} | XF:23ID1-VA{Mon-GV:1} | XF:23ID1-VA{Slt:1-GV:1}
REQUEST XF:23ID1-VA{Mon-GV:1} | XF:23ID1-VA{Mon-GV:1}
XF:23ID1-VA{Mir:3-CCG:1} | XF:23ID1-VA{Slt:1-GV:1} | XF:23ID1-VA{Mir:3-GV:1} | SHUTTER 1 | XF:23ID1-VA{Mon-GV:1}
XF:23ID1-VA{Mir:3-IP:1} | XF:23ID1-VA{Slt:1-GV:1} | XF:23ID1-VA{Mir:3-GV:1} | SHUTTER 1 | XF:23ID1-VA{Mon-GV:1}
XF:23ID1-VA{Mir:3-TCG:1} | XF:23ID1-VA{Slt:1-GV:1} | XF:23ID1-VA{Mir:3-GV:1}
REQUEST XF:23ID1-VA{Slt:1-GV:1} | XF:23ID1-VA{Slt:1-GV:1}
XF:23ID1-VA{Slt:2-CCG:1} | XF:23ID1-VA{Mir:3-GV:1}
XF:23ID1-VA{Slt:2-IP:1} | XF:23ID1-VA{Mir:3-GV:1}
XF:23ID1-VA{Diag:03-CCG:1} | XF:23ID1-VA{Mir:3-GV:1} | XF:23ID1-VA{Diag:03-GV:1} | XF:23ID1-VA{Slt:1-GV:1}
XF:23ID1-VA{Diag:03-IP:1} | XF:23ID1-VA{Mir:3-GV:1} | XF:23ID1-VA{Diag:03-GV:1} | XF:23ID1-VA{Slt:1-GV:1}
XF:23ID1-VA{Slt:2-TCG:1} | XF:23ID1-VA{Mir:3-GV:1}
XF:23ID1-VA{Diag:03-TCG:1} | XF:23ID1-VA{Mir:3-GV:1} | XF:23ID1-VA{Diag:03-GV:1}
REQUEST XF:23ID1-VA{Mir:3-GV:1} | XF:23ID1-VA{Mir:3-GV:1}
XF:23ID1-VA{SSh:2-CCG:1} | XF:23ID1-VA{Diag:03-GV:1} | XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{Diag:04-GV:1}
XF:23ID1-VA{SSh:2-IP:1} | XF:23ID1-VA{Diag:03-GV:1} | XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{Diag:04-GV:1}
XF:23ID1-VA{SSh:2-TCG:1} | XF:23ID1-VA{Diag:03-GV:1} | XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{Diag:04-GV:1}
FAST VALVE 1 TRIPPED | XF:23ID1-VA{Diag:03-GV:1} | XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{Diag:04-GV:1} | XF:23ID1-VA{DP:1-GV:1} | XF:23ID1-VA{Diag:05-GV:1} XF:23ID1-VA{Mir:3-GV:1} | XF:23ID1-VA{Diag:06-GV:1} XF:23ID1-VA{Slt:1-GV:1}
REQUEST XF:23ID1-VA{Diag:03-GV:1} | XF:23ID1-VA{Diag:03-GV:1}
XF:23ID1-VA{Diag:04-CCG:1} | XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{Diag:04-GV:1} | XF:23ID1-VA{Diag:03-GV:1}
XF:23ID1-VA{Diag:04-IP:1} | XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{Diag:04-GV:1} | XF:23ID1-VA{Diag:03-GV:1}
XF:23ID1-VA{Diag:04-TCG:1} | XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{Diag:04-GV:1}
REQUEST XF:23ID1-VA{SSh:2-GV:1} | XF:23ID1-VA{SSh:2-GV:1}
REQUEST XF:23ID1-VA{Diag:04-GV:1} | XF:23ID1-VA{Diag:04-GV:1}
XF:23ID1-VA{DP:1-CCG:1} | XF:23ID1-VA{DP:1-GV:1} | XF:23ID1-VA{Diag:04-GV:1} | XF:23ID1-VA{SSh:2-GV:1}
XF:23ID1-VA{DP:1-IP:1} | XF:23ID1-VA{DP:1-GV:1} | XF:23ID1-VA{Diag:04-GV:1} | XF:23ID1-VA{SSh:2-GV:1}
XF:23ID1-VA{Diag:05-CCG:1} | XF:23ID1-VA{DP:1-GV:1} | XF:23ID1-VA{Diag:05-GV:1} | XF:23ID1-VA{Diag:04-GV:1}
XF:23ID1-VA{Diag:05-IP:1} | XF:23ID1-VA{DP:1-GV:1} | XF:23ID1-VA{Diag:05-GV:1} | XF:23ID1-VA{Diag:04-GV:1}
XF:23ID1-VA{DP:1-TCG:1} | XF:23ID1-VA{DP:1-GV:1}
XF:23ID1-VA{Diag:05-TCG:1} | XF:23ID1-VA{DP:1-GV:1} | XF:23ID1-VA{Diag:05-GV:1}
REQUEST XF:23ID1-VA{DP:1-GV:1} | XF:23ID1-VA{DP:1-GV:1}
XF:23ID1-VA{Diag:06-CCG:1} | XF:23ID1-VA{Diag:05-GV:1} | XF:23ID1-VA{Diag:06-GV:1} | XF:23ID1-VA{DP:1-GV:1}
XF:23ID1-VA{Diag:06-IP:1} | XF:23ID1-VA{Diag:05-GV:1} | XF:23ID1-VA{Diag:06-GV:1} | XF:23ID1-VA{DP:1-GV:1}
XF:23ID1-VA{Diag:06-TCG:1} | XF:23ID1-VA{Diag:05-GV:1} | XF:23ID1-VA{Diag:06-GV:1}
REQUEST XF:23ID1-VA{Diag:05-GV:1} | XF:23ID1-VA{Diag:05-GV:1}
ENDSTATION 1 | XF:23ID1-VA{Diag:06-GV:1} | XF:23ID1-VA{Diag:05-GV:1} | XF:23ID1-VA{DP:1-GV:1}
REQUEST XF:23ID1-VA{Diag:06-GV:1} | XF:23ID1-VA{Diag:06-GV:1}
XF:23IDA-VA:2{SSh:1-CCG:1} | XF:23ID2-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23IDA-VA:2{SSh:1-IP:1} | XF:23ID2-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23ID2-VA{Diag:1-CCG:1} | XF:23ID2-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23ID2-VA{Diag:1-IP:1} | XF:23ID2-VA{Diag:01-GV:1} | FE SHUTTER | XF:23IDA-VA:2{Mir:1-GV:2} | XF:23IDA-VA:2{Mir:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:1} | XF:23IDA-VA:1{FS:1-GV:2}
XF:23ID2-VA{Mon:1-CCG:1} | XF:23ID2-VA{Diag:01-GV:1} | XF:23ID2-VA{Mon:1-GV:1} | SHUTTER 2 | XF:23IDA-VA:2{Mir:1-GV:2}
XF:23ID2-VA{Mon:1-IP:1} | XF:23ID2-VA{Diag:01-GV:1} | XF:23ID2-VA{Mon:1-GV:1} | SHUTTER 2 | XF:23IDA-VA:2{Mir:1-GV:2}
XF:23ID2-VA{Mon:1-TCG:1} | XF:23ID2-VA{Diag:01-GV:1} | XF:23ID2-VA{Mon:1-GV:1}
XF:23IDA-VA:2{SSh:1-TCG:1} | XF:23ID2-VA{Diag:01-GV:1}
XF:23ID2-VA{Diag:1-TCG:1} | XF:23ID2-VA{Diag:01-GV:1}
REQUEST XF:23ID2-VA{Diag:01-GV:1} | XF:23ID2-VA{Diag:01-GV:1}
XF:23ID2-VA{Slt:1-CCG:1} | XF:23ID2-VA{Mon:1-GV:1} | XF:23ID2-VA{Slt:1-GV:1} | SHUTTER 2 | XF:23ID2-VA{Diag:01-GV:1}
XF:23ID2-VA{Slt:1-IP:1} | XF:23ID2-VA{Mon:1-GV:1} | XF:23ID2-VA{Slt:1-GV:1} | SHUTTER 2 | XF:23ID2-VA{Diag:01-GV:1}
XF:23ID2-VA{Slt:1-TCG:1} | XF:23ID2-VA{Mon:1-GV:1} | XF:23ID2-VA{Slt:1-GV:1}
REQUEST XF:23ID2-VA{Mon:1-GV:1} | XF:23ID2-VA{Mon:1-GV:1}
XF:23ID2-VA{SSh:2-CCG:1} | XF:23ID2-VA{Slt:1-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1} | SHUTTER 2 | XF:23ID2-VA{Mon:1-GV:1}
XF:23ID2-VA{SSh:2-IP:1} | XF:23ID2-VA{Slt:1-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1} | SHUTTER 2 | XF:23ID2-VA{Mon:1-GV:1}
XF:23ID2-VA{Pmp:Inl:01-CCG:1} | XF:23ID2-VA{Slt:1-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1} | SHUTTER 2 | XF:23ID2-VA{Mon:1-GV:1}
XF:23ID2-VA{Pmp:Inl:01-IP:1} | XF:23ID2-VA{Slt:1-GV:1}
XF:23ID2-VA{SSh:2-TCG:1} | XF:23ID2-VA{Slt:1-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1}
XF:23ID2-VA{Pmp:Inl:01-TCG:1} | XF:23ID2-VA{Slt:1-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1}
REQUEST XF:23ID2-VA{Slt:1-GV:1} | XF:23ID2-VA{Slt:1-GV:1}
XF:23ID2-VA{Pmp:Inl:01-IP:01} | XF:23ID2-VA{Pmp:Inl:01-GV:1} | SHUTTER 2 | XF:23ID2-VA{Slt:1-GV:1} | XF:23ID2-VA{Mon:1-GV:1}
XF:23ID2-VA{Pmp:Inl:02-CCG:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1} | XF:23ID2-VA{Slt:1-GV:1}
XF:23ID2-VA{Pmp:Inl:02-IP:01} | XF:23ID2-VA{Pmp:Inl:01-GV:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1} | XF:23ID2-VA{Slt:1-GV:1}
XF:23ID2-VA{Pmp:Inl:02-TCG:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1}
REQUEST XF:23ID2-VA{Pmp:Inl:01-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1}
XF:23ID2-VA{Pmp:Inl:03-CCG:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1}
XF:23ID2-VA{Pmp:Inl:03-IP:01} | XF:23ID2-VA{Pmp:Inl:02-GV:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1} | XF:23ID2-VA{Pmp:Inl:01-GV:1}
XF:23ID2-VA{Pmp:Inl:03-TCG:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1}
FAST VALVE 2 | XF:23ID2-VA{Pmp:Inl:02-GV:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1} | XF:23ID2-VA{Diag:02-GV:1} XF:23ID2-VA{Mir:3-GV:1} | XF:23ID2-VA{Slt:2-GV:1} XF:23ID2-VA{Diag:03-GV:1} | XF:23ID2-VA{Chop-GV:1} XF:23ID2-VA{Pmp:Inl:01-GV:1} | XF:23ID2-VA{Slt:3-GV:1} XF:23ID2-VA{Slt:1-GV:1}
REQUEST XF:23ID2-VA{Pmp:Inl:02-GV:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1}
XF:23ID2-VA{Diag:02-CCG:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1} | XF:23ID2-VA{Diag:02-GV:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1}
XF:23ID2-VA{Diag:02-IP:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1} | XF:23ID2-VA{Diag:02-GV:1} | XF:23ID2-VA{Pmp:Inl:02-GV:1}
XF:23ID2-VA{Diag:02-TCG:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1} | XF:23ID2-VA{Diag:02-GV:1}
REQUEST XF:23ID2-VA{Pmp:Inl:03-GV:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1}
XF:23ID2-VA{Slt:2-CCG:1} | XF:23ID2-VA{Diag:02-GV:1} | XF:23ID2-VA{Slt:2-GV:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1}
XF:23ID2-VA{Slt:2-IP:01} | XF:23ID2-VA{Diag:02-GV:1} | XF:23ID2-VA{Slt:2-GV:1} | XF:23ID2-VA{Pmp:Inl:03-GV:1}
XF:23ID2-VA{Slt:2-TCG:1} | XF:23ID2-VA{Diag:02-GV:1} | XF:23ID2-VA{Slt:2-GV:1}
REQUEST XF:23ID2-VA{Diag:02-GV:1} | XF:23ID2-VA{Diag:02-GV:1}
XF:23ID2-VA{Chop-CCG:1} | XF:23ID2-VA{Slt:2-GV:1} | XF:23ID2-VA{Chop-GV:1} | XF:23ID2-VA{Diag:02-GV:1}
XF:23ID2-VA{Chop-IP:01} | XF:23ID2-VA{Slt:2-GV:1} | XF:23ID2-VA{Chop-GV:1} | XF:23ID2-VA{Diag:02-GV:1}
XF:23ID2-VA{Chop-TCG:1} | XF:23ID2-VA{Slt:2-GV:1} | XF:23ID2-VA{Chop-GV:1}
REQUEST XF:23ID2-VA{Slt:2-GV:1} | XF:23ID2-VA{Slt:2-GV:1}
XF:23ID2-VA{Slt:3-CCG:1} | XF:23ID2-VA{Chop-GV:1} | XF:23ID2-VA{Slt:3-GV:1} | XF:23ID2-VA{Slt:2-GV:1}
XF:23ID2-VA{Slt:3-IP:1} | XF:23ID2-VA{Chop-GV:1} | XF:23ID2-VA{Slt:3-GV:1} | XF:23ID2-VA{Slt:2-GV:1}
XF:23ID2-VA{GC-TCG:1} | XF:23ID2-VA{Chop-GV:1} | XF:23ID2-VA{Slt:3-GV:1} | XF:23ID2-VA{Slt:2-GV:1}
XF:23ID2-VA{Slt:3-TCG:1} | XF:23ID2-VA{Chop-GV:1}
REQUEST XF:23ID2-VA{Chop-GV:1} | XF:23ID2-VA{Chop-GV:1}
XF:23ID2-VA{Mir:3-CCG:1} | XF:23ID2-VA{Slt:3-GV:1} | XF:23ID2-VA{Mir:3-GV:1} | XF:23ID2-VA{Chop-GV:1}
XF:23ID2-VA{Mir:3-IP:1} | XF:23ID2-VA{Slt:3-GV:1} | XF:23ID2-VA{Mir:3-GV:1} | XF:23ID2-VA{Chop-GV:1}
REQUEST XF:23ID2-VA{Slt:3-GV:1} | XF:23ID2-VA{Slt:3-GV:1}
XF:23ID2-VA{Diag:03-CCG:1} | XF:23ID2-VA{Mir:3-GV:1} | XF:23ID2-VA{Diag:03-GV:1} | XF:23ID2-VA{Slt:3-GV:1}
XF:23ID2-VA{Diag:03-IP:1} | XF:23ID2-VA{Mir:3-GV:1} | XF:23ID2-VA{Diag:03-GV:1} | XF:23ID2-VA{Slt:3-GV:1}
REQUEST XF:23ID2-VA{Mir:3-GV:1} | XF:23ID2-VA{Mir:3-GV:1}
ENDSTATION 2 | XF:23ID2-VA{Diag:03-GV:1} | XF:23ID2-VA{Mir:3-GV:1} | XF:23ID2-VA{Slt:3-GV:1}
XF:23ID2-VA{Diag:03-TCG:1} | XF:23ID2-VA{Diag:03-GV:1}
REQUEST XF:23ID2-VA{Diag:03-GV:1} | XF:23ID2-VA{Diag:03-GV:1}
DXF:23ID2-VA{GC-GV:1} | XF:23ID2-VA{GC-GV:3}
DXF:23ID2-VA{GC-GV:2} | XF:23ID2-VA{GC-GV:3}
OPENXF:23ID2-VA{GC-GV:1} | XF:23ID2-VA{GC-GV:3}
OPENXF:23ID2-VA{GC-GV:2} | XF:23ID2-VA{GC-GV:3}

## PLC EPS ES IO
Index | Component | Signal | Source | Pins | Destination | Pins | PLC Tag Name | Tag is Alias for: | Temp:emulation | Array element in Global tag | DINT used
1 | XF:23ID1-VA{Dif-IP:1} | Sts:Rly1PLC-Sts | XF:23ID1-EPS{Armor:E3} Ch2 |  | XF:23ID1-EPS{ES:Armor:E3} Ch2 |  | ID1_VA_Dif_IP1 | Armor_E3:I.Data.2 |  | IP_Sts_1[0] | 1
2 | XF:23ID1-VA{Dif-IP:2} | Sts:Rly1PLC-Sts | XF:23ID1-EPS{Armor:E3} Ch3 |  | XF:23ID1-EPS{ES:Armor:E3} Ch3 |  | ID1_VA_Dif_IP2 | Armor_E3:I.Data.3 | Local:1:I.Data.1 | IP_Sts_1[1]
3 | XF:23ID1-VA{Dif-TMP:1} | Sts:Rly1PLC-Sts | NPT 10 | 5, 6 | XF:23ID1-EPS{ES:Armor:Hlf} Ch0 |  | ID1_VA_Dif_TMP1 | Armor_Hlf:I.Data.4 |  | IP_Sts_1[2]
4 | XF:23ID1-VA{Dif-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-EPS{Armor:E3} Ch4 |  | XF:23ID1-EPS{ES:Armor:E3} Ch4 |  | ID1_VA_Dif_CCG1 | Armor_E3:I.Data.4 |  | CCG_Sts_1[0] | 1
5 | XF:23ID1-VA{Dif:LoadLck-CCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-EPS{Armor:E3} Ch5 |  | XF:23ID1-EPS{ES:Armor:E3} Ch5 |  | ID1_VA_DifLoadLck_CCG1 | Armor_E3:I.Data.5 |  | CCG_Sts_1[1]
6 | XF:23ID1-VA{Dif-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-EPS{Armor:E3} Ch6 |  | XF:23ID1-EPS{ES:Armor:E3} Ch6 |  | ID1_VA_Dif_TCG1 | Armor_E3:I.Data.6 |  | TCG_Sts_1[0] | 1
7 | XF:23ID1-VA{Dif:LoadLck-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-EPS{Armor:E3} Ch7 |  | XF:23ID1-EPS{ES:Armor:E3} Ch7 |  | ID1_VA_DifLoadLck_TCG1 | Armor_E3:I.Data.7 |  | TCG_Sts_1[1]
8 | XF:23ID1-VA{Dif:Backing-TCG:1} | Sts:Rly1PLC-Sts | XF:23ID1-EPS{Armor:E3} Ch8 |  | XF:23ID1-EPS{ES:Armor:E3} Ch7 |  | ID1_VA_DifBacking_TCG1 | Armor_E3:I.Data.8 |  | TCG_Sts_1[2]
8 | XF:23ID1-VA{Dif-GV:2} | Sw:OpnLim-Sts | XF:23ID1-VA{Dif-GV:2} |  | XF:23ID1-EPS{ES:Armor:1} Ch0 |  | ID1_VA_Dif_GV2_Opn | Armor_01:I.Data.0 |  | GV_02_Sts.OpnSw | 1
9 | XF:23ID1-VA{Dif-GV:3} | Sw:OpnLim-Sts | XF:23ID1-VA{Dif-GV:3} |  | XF:23ID1-EPS{ES:Armor:1} Ch4 |  | ID1_VA_Dif_GV3_Opn | Armor_01:I.Data.4 |  | GV_03_Sts.OpnSw | 1
10 | XF:23ID1-VA{Dif-GV:4} | Sw:OpnLim-Sts | XF:23ID1-VA{Dif-GV:4} |  | XF:23ID1-EPS{ES:Armor:1} Ch8 |  | ID1_VA_Dif_GV4_Opn | Armor_01:I.Data.8 |  | GV_04_Sts.OpnSw | 1
11 | XF:23ID1-VA{Dif-GV:5} | Sw:OpnLim-Sts | XF:23ID1-VA{Dif-GV:5} |  | XF:23ID1-EPS{ES:Armor:1} Ch12 |  | ID1_VA_Dif_GV5_Opn | Armor_01:I.Data.12 |  | GV_05_Sts.OpnSw | 1
12 | XF:23ID1-VA{Dif-GV:6} | Sw:OpnLim-Sts | XF:23ID1-VA{Dif-GV:6} |  | XF:23ID1-EPS{ES:Armor:4} Ch0 |  | ID1_VA_Dif_GV6_Opn | Armor_04:I.Data.0 |  | GV_06_Sts.OpnSw | 1
13 | XF:23ID1-VA{Dif-GV:7} | Sw:OpnLim-Sts | XF:23ID1-VA{Dif-GV:7} |  | XF:23ID1-EPS{ES:Armor:7} Ch8 |  | ID1_VA_Dif_GV7_Opn | Armor_07:I.Data.8 |  | GV_08_Sts.OpnSw | 1
13 | XF:23ID1-VA{Dif-GV:2} | Sw:ClsLim-Sts | XF:23ID1-VA{Dif-GV:2} |  | XF:23ID1-EPS{ES:Armor:1} Ch1 |  | ID1_VA_Dif_GV2_Cls | Armor_01:I.Data.1 |  | GV_02_Sts.ClsSw
14 | XF:23ID1-VA{Dif-GV:3} | Sw:ClsLim-Sts | XF:23ID1-VA{Dif-GV:3} |  | XF:23ID1-EPS{ES:Armor:1} Ch5 |  | ID1_VA_Dif_GV3_Cls | Armor_01:I.Data.5 |  | GV_03_Sts.ClsSw
15 | XF:23ID1-VA{Dif-GV:4} | Sw:ClsLim-Sts | XF:23ID1-VA{Dif-GV:4} |  | XF:23ID1-EPS{ES:Armor:1} Ch9 |  | ID1_VA_Dif_GV4_Cls | Armor_01:I.Data.9 |  | GV_04_Sts.ClsSw
16 | XF:23ID1-VA{Dif-GV:5} | Sw:ClsLim-Sts | XF:23ID1-VA{Dif-GV:5} |  | XF:23ID1-EPS{ES:Armor:1} Ch13 |  | ID1_VA_Dif_GV5_Cls | Armor_01:I.Data.13 |  | GV_05_Sts.ClsSw
17 | XF:23ID1-VA{Dif-GV:6} | Sw:ClsLim-Sts | XF:23ID1-VA{Dif-GV:6} |  | XF:23ID1-EPS{ES:Armor:4} Ch1 |  | ID1_VA_Dif_GV6_Cls | Armor_04:I.Data.1 |  | GV_06_Sts.ClsSw
18 | XF:23ID1-VA{Dif-GV:8} | Sw:ClsLim-Sts | XF:23ID1-VA{Dif-GV:8} |  | XF:23ID1-EPS{ES:Armor:7} Ch9 |  | ID1_VA_Dif_GV8_Cls | Armor_07:I.Data.9 |  | GV_08_Sts.ClsSw
18 | XF:23ID1-VA{Dif-GV:2} | Sts:Coil-Sts | XF:23ID1-VA{Dif-GV:2} |  | XF:23ID1-EPS{ES:Armor:1} Ch2 |  | ID1_VA_Dif_GV2_Coil | Armor_01:O.Data.2 |  | GV_02_Sts.Coil1
19 | XF:23ID1-VA{Dif-GV:3} | Sts:Coil-Sts | XF:23ID1-VA{Dif-GV:3} |  | XF:23ID1-EPS{ES:Armor:1} Ch6 |  | ID1_VA_Dif_GV3_Coil | Armor_01:O.Data.6 |  | GV_03_Sts.Coil1
20 | XF:23ID1-VA{Dif-GV:4} | Sts:Coil-Sts | XF:23ID1-VA{Dif-GV:4} |  | XF:23ID1-EPS{ES:Armor:1} Ch10 |  | ID1_VA_Dif_GV4_Coil | Armor_01:O.Data.10 |  | GV_04_Sts.Coil1
21 | XF:23ID1-VA{Dif-GV:5} | Sts:Coil-Sts | XF:23ID1-VA{Dif-GV:5} |  | XF:23ID1-EPS{ES:Armor:1} Ch14 |  | ID1_VA_Dif_GV5_Coil | Armor_01:O.Data.14 |  | GV_05_Sts.Coil1
22 | XF:23ID1-VA{Dif-GV:6} | Sts:Coil-Sts | XF:23ID1-VA{Dif-GV:6} |  | XF:23ID1-EPS{ES:Armor:4} Ch2 |  | ID1_VA_Dif_GV6_Coil1 | Armor_04:O.Data.2 |  | GV_06_Sts.Coil1
23 |  |  |  |  | XF:23ID1-EPS{ES:Armor:4} Ch3 |  | ID1_VA_Dif_GV6_Coil2 | Armor_04:O.Data.3 |  | GV_06_Sts.Coil2
24 | XF:23ID1-VA{Dif-Vlv:7} | Sts:Coil-Sts |  |  | XF:23ID1-EPS{ES:Armor:4} Ch14 |  | ID1_VA_Dif_Vlv7_Coil1 | Armor_04:O.Data.14 |  | GV_07_Sts.Coil1
25 | XF:23ID1-VA{Dif-GV:8} | Sts:Coil-Sts | XF:23ID1-VA{Dif-GV:8} |  | XF:23ID1-EPS{ES:Armor:7} Ch10 |  | ID1_VA_Dif_GV6_Coil1 | Armor_07:O.Data.10 |  | GV_08_Sts.Coil1
26 |  |  |  |  | XF:23ID1-EPS{ES:Armor:7} Ch11 |  | ID1_VA_Dif_GV6_Coil2 | Armor_04:O.Data.11 |  | GV_08_Sts.Coil2
24 | XF:23ID1-CT{Dif-LoadLck-Trans} | Sw:NO-Sts | Retracted |  | XF:23ID1-EPS{ES:Armor:4} Ch4 |  | Sample_Transfer_NO | Armor_04:I.Data.4 |  | Misc_Sts_1[0] | 1
25 | XF:23ID1-CT{Dif-LoadLck-Trans} | Sw:NC-Sts | Not Retracted |  | XF:23ID1-EPS{ES:Armor:4} Ch5 |  | Sample_Transfer_NC | Armor_04:I.Data.5 |  | Misc_Sts_1[1]
23 | XF:23ID1-CT{PLC:ES}Out:VaES-Sts |  | XF:23ID1-EPS{ES:Armor:E3} Ch0 |  | XF:23ID1-EPS{Armor:E3} Ch0 |  | Vac_Sts_to_BL | Armor_E3:O.Data.0 |  | Misc_Sts_1[2]
24 | XF:23ID1-CT{PLC:ES}In:VaBL-Sts |  | XF:23ID1-EPS{Armor:E3} Ch1 |  | XF:23ID1-EPS{ES:Armor:E3} Ch1 |  | Vac_Sts_from_BL | Armor_E3:I.Data.1 |  | Misc_Sts_1[3]
25 | XF:23ID1-VA{Dif-TMP:1} | Sts:Operation-Sts | XF:23ID1-VA{Dif-TMP:1}Sts:Operation-Sts |  |  |  | STP_Normal_Sts | Armor_Hlf:I.Data.0 |  | Misc_Sts_1[4]
26 | XF:23ID1-VA{Dif-TMP:1} | Sts:Alarm-Sts | XF:23ID1-VA{Dif-TMP:1}Sts:Alarm-Sts |  |  |  | STP_Alarm_Sts | Armor_Hlf:I.Data.1 |  | Misc_Sts_1[5]
27 | XF:23ID1-VA{Dif-TMP:1} | Cmd:Start-Cmd | XF:23ID1-VA{Dif-TMP:1}Cmd:Start-Cmd |  |  |  | STP_Start_Cmd | Armor_Hlf:O.Data.2 |  | Misc_Sts_1[6]
28 | XF:23ID1-VA{Dif-TMP:1} | Cmd:Reset-Cmd | XF:23ID1-VA{Dif-TMP:1}Cmd:Reset-Cmd |  |  |  | STP_Reset_Cmd | Armor_Hlf:O.Data.3 |  | Misc_Sts_1[7]
29 | XF:23ID1-VA{Dif:LoadLck-TMP:1} | Sts:Operation-Sts | XF:23ID1-VA{Dif:LoadLck-TMP:1}Sts:Operation-Sts |  |  |  | NPT_Normal_Sts | Armor_Hlf:I.Data.4 |  | Misc_Sts_1[8]
30 | XF:23ID1-VA{Dif:LoadLck-TMP:1} | Cmd:Start-Cmd | XF:23ID1-VA{Dif:LoadLck-TMP:1}Cmd:Start-Cmd |  |  |  | NPT_Start_Cmd | Armor_Hlf:O.Data.5 |  | Misc_Sts_1[9]
31 | XF:23ID1-VA{Dif:DifSeal-TMP:1} | Sts:Operation-Sts | XF:23ID1-VA{Dif:DifSeal-TMP:1}Sts:Operation-Sts |  |  |  | DifSeal_Normal_Sts | Armor_Hlf:I.Data.6 |  | Misc_Sts_2[0]
32 | XF:23ID1-VA{Dif:DifSeal-TMP:1} | Cmd:Start-Cmd | XF:23ID1-VA{Dif:DifSeal-TMP:1}Cmd:Start-Cmd |  |  |  | DifSeal_Start_Cmd | Armor_Hlf:O.Data.7 |  | Misc_Sts_2[1]
31 | XF:23ID1-ES{Dif:LoadLck-Trans} | Pos-Sts | XF:23ID1-ES{Dif:LoadLck-Trans}Pos-Sts |  |  |  | Sample_Transfer_Sts |  |  | Misc_Sts_1[10]
32 | XF:23ID1-ES{Dif:LoadLck-Trans} | Sts:Flt-Sts | XF:23ID1-ES{Dif:LoadLck-Trans}Sts:Flt-Sts |  |  |  | Sample_Transfer_Flt |  |  | Misc_Sts_1[11]
33 | XF:23ID1-ES{LED:1} | Sw-Cmd |  |  |  |  | ID1_ES_LED1_Cmd | Armor_04:O.Data.6 |  | Misc_Sts_1[12]
34 | XF:23ID1-ES{LED:2} | Sw-Cmd |  |  |  |  | ID1_ES_LED2_Cmd | Armor_04:O.Data.7 |  | Misc_Sts_1[13]
35 | XF:23ID1-ES{Dif-FS} | Sw:OutLim-Sts | YAG |  |  |  | ID1_ES_Dif_FS_Out | Armor_04:I.Data.11 |  | Act_01_Sts.ClsSw
36 | XF:23ID1-ES{Dif-FS} | Sw:InLim-Sts | YAG |  |  |  | ID1_ES_Dif_FS_In | Armor_04:I.Data.10 |  | Act_01_Sts.InSw
37 | XF:23ID1-ES{Dif-FS} | Sts:Act-Sts | YAG |  |  |  | ID1_ES_Dif_FS_Act | Armor_04:O.Data.8 |  | Act_01_Sts.Coil1
38 | XF:23ID1-ES{Dif-Abs} | Sw:OutLim-Sts | TiO2 |  |  |  | ID1_ES_Dif_Abs_Out | Armor_04:I.Data.13 |  | Act_02_Sts.InSw
39 | XF:23ID1-ES{Dif-Abs} | Sw:InLim-Sts | TiO3 |  |  |  | ID1_ES_Dif_Abs_In | Armor_04:I.Data.12 |  | Act_02_Sts.OpnSw
40 | XF:23ID1-ES{Dif-Abs} | Sts:Act-Sts | TiO4 |  |  |  | ID1_ES_Dif_Abs_Act | Armor_04:O.Data.9 |  | Act_02_Sts.Coil1
| XF:23ID1-ES{FCCD-PSU}Sw-Sel | [5 empty] | ID1_ES_FCCD_PSUSw_Sel | Armor_07:O.Data.0
| XF:23ID1-ES{FCCD-PSU}Sw-Sts | [5 empty] | ID1_ES_FCCD_PSUSw_Sts | Armor_07:I.Data.1
| XF:23ID1-ES{FCCD-N2}Sw:Main-Sel | [5 empty] | ID1_ES_FCCD_N2SwMain_Sel | Armor_07:O.Data.2
| XF:23ID1-ES{FCCD-N2}Sw:Main-Sts | [5 empty] | ID1_ES_FCCD_N2SwMain_Sts | Armor_07:I.Data.3
| XF:23ID1-ES{FCCD-N2}Sw:Gas-Sel | [5 empty] | ID1_ES_FCCD_N2SwGas_Sel | Armor_07:O.Data.4
| XF:23ID1-ES{FCCD-N2}Sw:Gas-Sts | [5 empty] | ID1_ES_FCCD_N2SwGas_Sts | Armor_07:I.Data.5
| XF:23ID1-ES{FCCD-CIN}Sw:FP-Sel | [5 empty] | ID1_ES_FCCD_CINSwFP_Sel | Armor_07:O.Data.6
| XF:23ID1-ES{FCCD-CIN}Sw:FP-Sts | [5 empty] | ID1_ES_FCCD_CINSwFP_Sts | Armor_07:I.Data.7
| XF:23ID1-VA{Dif-TMP:2}SpeedSP-Sts | [5 empty] | ID1_VA_Dif_TMP2_Sts | Armor_07:I.Data.13 |  | Misc_Sts_1[29]
| XF:23ID1-ES{Dif-Ax:Gam}T-I | [5 empty] | ID1_ES_Dif_AxGamT_I | Armor_05:I.Ch0Data |  | T_I[0]
| XF:23ID1-VA{Dif-TMP:2}DriveMotor-Cmd | [5 empty] | ID1_VA_Dif_TMP2_Motor | Armor_07:O.Data.15
| XF:23ID1-VA{Dif-TMP:2}Standby-Cmd | [5 empty] | ID1_VA_Dif_TMP2_Standby | Armor_07:O.Data.12
| XF:23ID1-VA{Dif-TMP:2}VentEna-Cmd | [5 empty] | ID1_VA_Dif_TMP2_VentEna | Armor_07:O.Data.14
| XF:23ID1-OP{Sh:Fast}T-I | [5 empty] | ID1_OP_ShFastT_I | Armor_05:I.Ch1Data |  | T_I[1]
| XF:23ID1-OP{FCCD-N2}T-I | [5 empty] | ID1_OP_FCCD_N2T_I | Armor_06:I.Ch0Data |  | T_I[2]